## Slide 1: Air Conditioning the Middle School: Rationale and Proposal
Presented by the Regional School Committee

## Slide 2: History
MS opened in April 2003
  Originally designed for AC; removed from plan for $
  No adjustments to plan, no pre-installation of pipes or ducts
Ongoing complaints of heat buildup in classrooms during hot periods, especially when humid

## Slide 3: Floor plan
  42 classrooms, most fully occupied throughout the day
  1st floor: 12 (incl 7 HS)
  2nd floor: 30
Existing AC: office suite, computer lab, 202A, HS bio labs

## Slide 4: What is the right temperature?
Reading speed and comprehension as much as 30% worse at 81°F compared to 68°F
    “Temperature and School Work Performance,” Lawrence Berkeley National Laboratory
Performance on numerical and language tasks significantly worse at 77°F compared to 68 °F
    “The effects of moderately raised classroom temperatures and classroom ventilation rate on the performance of schoolwork by children,” HVAC & R Research 2007
BUT, our problem is NOT trying to reach 68°. It’s trying to reach 78°.

## Slide 5: Temperature Data 2010-11
Temperature is recorded hourly in each MS classroom
We analyzed data for 2010-2011, focusing on:
  May, June, September
  Weekdays, 7 AM – 4 PM, when school is in session
Color-coded by
temperature:
  78-80: yellow
  80-85: orange
  85-90: red
  >90: black
  Some glitches in data capture (if temp constant >4 hours, gray)
  Some gaps in early data (missing some of the worst classrooms)

## Slide 6: For example…
Date | Time | Rm 236 | Rm 237 | Rm238
9/7/2010 | 7:00:00 AM | 79.27 | 77.97 | 73.75
9/7/2010 | 8:00:00 AM | 79.27 | 77.97 | 74.51
9/7/2010 | 9:00:00 AM | 79.57 | 79.18 | 76.91
9/7/2010 | 10:00:00 AM | 81.14 | 80.25 | 79.05
9/7/2010 | 11:00:00 AM | 81.73 | 80.44 | 80.5
9/7/2010 | 12:00:00 PM | 82.36 | 80.54 | 81.06
9/7/2010 | 1:00:00 PM | 83.13 | 81.89 | 82.02
9/7/2010 | 2:00:00 PM | 84.58 | 83.27 | 82.84
9/7/2010 | 3:00:00 PM | 85.08 | 84.53 | 84.06
9/7/2010 | 4:00:00 PM | 85.08 | 83.91 | 84.26

## Slide 7: 2010: 5/17-5/21
Date | Time | U103RmTemp.PointValue | U105RmTemp.PointValue | U106RmTemp.PointValue | U107RmTemp.PointValue | U109RmTemp.PointValue | U120RmTemp.PointValue | U122ERmTemp.PointValue | U123RmTemp.PointValue | U124RmTemp.PointValue | U125RmTemp.PointValue | 204 | 205 | 207 | 209 | 211 | 212 | U227RmTemp.PointValue | U228RmTemp.PointValue | U229RmTemp.PointValue | U230RmTemp.PointValue | U232RmTemp.PointValue | U233RmTemp.PointValue | U234RmTemp.PointValue | U235RmTemp.PointValue | U236RmTemp.PointValue | U237RmTemp.PointValue | U238RmTemp.PointValue
5/17/2010 | 6:00:00 AM | 74.57 | 74.7 | 73.72 | 61.32 | 76.42 | 81.71 | 73.52 | 74.71 | 74.83 | 78.53 |  |  |  |  |  |  | 80.26 | 80.09 | 79.44 | 78.04 | 72.17 |  | 78.75 | 77.29 | 77.24 | 77.02 | 78.51
5/17/2010 | 7:00:00 AM | 71.82 | 73.43 | 70.21 | 62.9 | 75.88 | 80.71 | 72.02 | 73.54 | 71.2 | 73.86 |  |  |  |  |  |  | 77.7 | 77.02 | 78.81 | 73.84 | 71.15 |  | 76.79 | 73.96 | 74.24 | 73.01 | 74.98
5/17/2010 | 8:00:00 AM | 71.56 | 73.52 | 70.31 | 64.29 | 75.88 | 80.13 | 72.29 | 73.73 | 71.59 | 74.42 |  |  |  |  |  |  | 77.7 | 76.62 | 78.64 | 73.76 | 72.33 |  | 77.25 | 74.58 | 74.89 | 74.12 | 75.69
5/17/2010 | 9:00:00 AM | 73.37 | 75.38 | 73.48 | 66.03 | 76.24 | 80.9 | 73.92 | 75.93 | 73.29 | 76.17 |  |  |  |  |  |  | 78.76 | 78.29 | 78.99 | 76.04 | 75.03 |  | 79.82 | 77.79 | 77.77 | 77.43 | 78.38
5/17/2010 | 10:00:00 AM | 75.15 | 77.01 | 75.45 | 67.82 | 77.6 | 81.67 | 74.7 | 77.59 | 75.14 | 77.15 |  |  |  |  |  |  | 79.92 | 79.5 | 80.05 | 78 | 77.3 |  | 81.84 | 80.1 | 80 | 79.19 | 80.3
5/17/2010 | 11:00:00 AM | 76.14 | 77.82 | 76.19 | 69.02 | 78.2 | 80.53 | 75.41 | 77.61 | 75.86 | 77.32 |  |  |  |  |  |  | 80.03 | 80.54 | 81.21 | 79.09 | 78.25 |  | 82.47 | 81.34 | 81.18 | 80.06 | 81.15
5/17/2010 | 12:00:00 PM | 76.91 | 78.15 | 77.28 | 70.08 | 78.29 | 78.6 | 75.23 | 77.61 | 76.3 | 77.32 |  |  |  |  |  |  | 80.03 | 80.6 | 82.39 | 78.53 | 78.29 |  | 82.87 | 81.47 | 81.18 | 80.46 | 81.15
5/17/2010 | 1:00:00 PM | 77.4 | 77.31 | 77.75 | 70.37 | 79.01 | 78.17 | 75.05 | 77.61 | 76.34 | 77.32 |  |  |  |  |  |  | 80.68 | 81.41 | 82.68 | 79.12 | 78.29 |  | 83.33 | 82.16 | 82.01 | 81.9 | 81.45
5/17/2010 | 2:00:00 PM | 77.4 | 77.31 | 77.75 | 70.37 | 79.01 | 78.4 | 75.75 | 77.84 | 77.08 | 77.32 |  |  |  |  |  |  | 80.87 | 82.09 | 83.92 | 79.9 | 78.98 |  | 83.33 | 82.81 | 82.01 | 82.59 | 82.46
5/17/2010 | 3:00:00 PM | 77.4 | 77.88 | 77.75 | 71.03 | 79.68 | 79.02 | 75.9 | 78.45 | 77.08 | 77.32 |  |  |  |  |  |  | 81.39 | 82.6 | 84.4 | 80 | 79.11 |  | 83.33 | 82.68 | 82.76 | 82.47 | 82.6
5/17/2010 | 4:00:00 PM | 77 | 77.58 | 76.93 | 71.07 | 79.83 | 79.07 | 75.59 | 77.41 | 77.08 | 77.32 |  |  |  |  |  |  | 82.5 | 83.4 | 84.4 | 80.95 | 79.11 |  | 83.33 | 82.28 | 82.84 | 81.76 | 82.06
5/18/2010 | 7:00:00 AM | 73.16 | 74.1 | 71.63 | 65.1 | 78.09 | 81.08 | 73.09 | 75.13 | 72.57 | 74.18 |  |  |  |  |  |  | 76.54 | 77.46 | 80.66 | 75.07 | 73.15 |  | 78.1 | 75.57 | 75.18 | 68.38 | 75.05
5/18/2010 | 8:00:00 AM | 72.65 | 73.1 | 70.92 | 65.86 | 78.09 | 80.1 | 72.74 | 74.52 | 71.03 | 73.98 |  |  |  |  |  |  | 75.68 | 76.55 | 79.76 | 73.78 | 73.01 |  | 77.55 | 74.89 | 74.94 | 69.87 | 74.26
5/18/2010 | 9:00:00 AM | 72.65 | 74.27 | 72.17 | 66.54 | 78.26 | 80.04 | 72.74 | 75.67 | 71.85 | 74.05 |  |  |  |  |  |  | 77.37 | 77.55 | 79.58 | 75.3 | 73.96 |  | 78.81 | 76.17 | 76.05 | 72.68 | 75.45
5/18/2010 | 10:00:00 AM | 72.65 | 75.63 | 73.23 | 67.49 | 77.9 | 79.47 | 72.74 | 76.53 | 72.38 | 74.14 |  |  |  |  |  |  | 78.04 | 77.96 | 80.18 | 76.17 | 75.1 |  | 79.57 | 77.3 | 76.71 | 73.46 | 75.85
5/18/2010 | 11:00:00 AM | 73.43 | 75.09 | 73.61 | 68.39 | 77.64 | 79.22 | 74.06 | 77.26 | 73.02 | 74.27 |  |  |  |  |  |  | 78.56 | 78.78 | 80.58 | 76.91 | 75.97 |  | 80.35 | 78.27 | 76.96 | 74.23 | 76.81
5/18/2010 | 12:00:00 PM | 74.14 | 75.66 | 74.27 | 69.23 | 78.05 | 78.5 | 74.28 | 77.55 | 73.41 | 74.27 |  |  |  |  |  |  | 78.99 | 78.83 | 80.99 | 76.57 | 76.86 |  | 81.08 | 78.84 | 77.1 | 74.64 | 77.15
5/18/2010 | 1:00:00 PM | 74.14 | 75.66 | 74.63 | 70.15 | 78.14 | 78.8 | 74.28 | 77.55 | 73.41 | 74.27 |  |  |  |  |  |  | 79.35 | 78.83 | 80.99 | 77.61 | 76.76 |  | 81.54 | 79.51 | 77.74 | 75.95 | 77.39
5/18/2010 | 2:00:00 PM | 74.14 | 75.15 | 74.89 | 70.16 | 78.84 | 78.94 | 74.9 | 77.55 | 74.12 | 73.83 |  |  |  |  |  |  | 79.35 | 79.23 | 80.99 | 76.63 | 77.09 |  | 81.54 | 80.22 | 77.74 | 75.35 | 77.89
5/18/2010 | 3:00:00 PM | 74.14 | 74.07 | 74.26 | 69.74 | 78.33 | 78.34 | 73.98 | 77.55 | 74.12 | 73.47 |  |  |  |  |  |  | 79.96 | 79.3 | 80.99 | 76.28 | 76.77 |  | 81.3 | 79.92 | 77.18 | 74.79 | 77.17
5/18/2010 | 4:00:00 PM | 73.76 | 73.18 | 73.33 | 69.46 | 77.13 | 78.06 | 73.16 | 76.71 | 73.01 | 73.74 |  |  |  |  |  |  | 79.36 | 77.68 | 80.99 | 75.02 | 75.13 |  | 80.72 | 77.99 | 75.66 | 73.67 | 76.08
5/19/2010 | 7:00:00 AM | 71.38 | 73.27 | 69.59 | 62.36 | 72.24 | 76.23 | 72.02 | 72.18 | 69.32 | 73.47 |  |  |  |  |  |  | 72.88 | 71.64 | 77.03 | 69.96 | 67.09 |  | 72.71 | 71.44 | 71.25 | 67.97 | 70.67
5/19/2010 | 8:00:00 AM | 70.68 | 73.25 | 68.53 | 63.25 | 72.24 | 75.68 | 72.02 | 72.17 | 69.35 | 73.2 |  |  |  |  |  |  | 72.12 | 71.11 | 76.47 | 70.08 | 67.3 |  | 72 | 70.86 | 71.02 | 67.57 | 70.11
5/19/2010 | 9:00:00 AM | 70.33 | 74 | 68.3 | 64.2 | 72.69 | 75.44 | 72.02 | 73.59 | 70.43 | 73.33 |  |  |  |  |  |  | 72.91 | 72.05 | 76.19 | 71.84 | 68.79 |  | 73.21 | 72.12 | 71.97 | 69.21 | 70.93
5/19/2010 | 10:00:00 AM | 70.33 | 73.94 | 69.48 | 64.43 | 73.43 | 75.44 | 72.02 | 74.37 | 70.89 | 73.68 |  |  |  |  |  |  | 73.17 | 72.98 | 76.19 | 72.79 | 70.08 |  | 73.57 | 72.67 | 71.8 | 69.44 | 71.41
5/19/2010 | 11:00:00 AM | 71.15 | 73.33 | 69.66 | 64.43 | 74.04 | 75.44 | 72.53 | 75.05 | 70.89 | 73.92 |  |  |  |  |  |  | 72.71 | 74 | 76.86 | 73.67 | 70.68 |  | 73.76 | 73.1 | 72.19 | 70.61 | 72.27
5/19/2010 | 12:00:00 PM | 71.82 | 73.97 | 70.36 | 65 | 74.77 | 75.44 | 72.76 | 73.61 | 70.64 | 73.89 |  |  |  |  |  |  | 72.92 | 73.29 | 76.97 | 72.61 | 70.72 |  | 74.85 | 72.88 | 71.7 | 70.18 | 72.14
5/19/2010 | 1:00:00 PM | 71.82 | 73.24 | 70.07 | 65.08 | 75.23 | 75.44 | 72.76 | 72.79 | 70.12 | 73.99 |  |  |  |  |  |  | 73.31 | 73.78 | 76.97 | 73.68 | 71.05 |  | 74.62 | 73.56 | 72.26 | 71.58 | 71.71
5/19/2010 | 2:00:00 PM | 71.82 | 73.23 | 69.96 | 65.17 | 75.33 | 75.44 | 73.47 | 74.05 | 70.4 | 73.72 |  |  |  |  |  |  | 72.7 | 73.83 | 77.26 | 73.54 | 71.89 |  | 75.35 | 73.55 | 72.11 | 70.35 | 72.35
5/19/2010 | 3:00:00 PM | 71.82 | 73.23 | 70.93 | 65.75 | 72.71 | 74.92 | 73.5 | 74.86 | 70.01 | 73.69 |  |  |  |  |  |  | 73.34 | 73.69 | 77.75 | 74.33 | 71.41 |  | 75.12 | 72.6 | 72.06 | 70.1 | 72.21
5/19/2010 | 4:00:00 PM | 71.12 | 73.23 | 70.8 | 65.75 | 70.97 | 74.68 | 73.5 | 74.58 | 69.47 | 73.19 |  |  |  |  |  |  | 72.67 | 72.3 | 77.75 | 72.72 | 69.96 |  | 74.09 | 71.53 | 71.43 | 68.8 | 71.03
5/20/2010 | 7:00:00 AM | 72.62 | 73.25 | 68.22 | 61.31 | 65.97 | 74.34 | 71.24 | 70.34 | 68.18 | 73.28 |  |  |  |  |  |  | 69.7 | 70.05 | 74.17 | 70.49 | 66.47 |  | 71.02 | 69.4 | 69.38 | 67.79 | 69.24
5/20/2010 | 8:00:00 AM | 72.57 | 73.32 | 68.43 | 62.75 | 66.06 | 74.27 | 71.35 | 70.74 | 68.3 | 73.3 |  |  |  |  |  |  | 69.75 | 69.86 | 73.92 | 70.02 | 68.16 |  | 71.83 | 70.42 | 70.03 | 69.43 | 70.1
5/20/2010 | 9:00:00 AM | 73.97 | 74.49 | 70.86 | 64.91 | 67.59 | 75.03 | 72.34 | 73.57 | 71.52 | 74.48 |  |  |  |  |  |  | 71.22 | 71.54 | 74.17 | 71.06 | 71.09 |  | 73.76 | 73.64 | 72.6 | 73.76 | 72.93
5/20/2010 | 10:00:00 AM | 75.16 | 75.65 | 71.97 | 65.94 | 68.76 | 100 | 73.47 | 75.14 | 73.39 | 74.58 |  |  |  |  |  |  | 71.8 | 72.64 | 75.19 | 71.72 | 73.4 |  | 76.09 | 75.48 | 74.66 | 76.11 | 76.44
5/20/2010 | 11:00:00 AM | 76.21 | 76.67 | 74.03 | 67.11 | 68.76 | 100 | 74.24 | 75.7 | 74.16 | 74.58 |  |  |  |  |  |  | 73.36 | 73.98 | 75.87 | 73.83 | 74.72 |  | 77.63 | 77.85 | 76.35 | 77.59 | 78.31
5/20/2010 | 12:00:00 PM | 77.14 | 77.68 | 75.65 | 68.1 | 69.11 | 100 | 74.96 | 76.2 | 75.08 | 74.58 |  |  |  |  |  |  | 74.66 | 74.47 | 76.96 | 74.73 | 75.82 |  | 78.99 | 78.43 | 77.24 | 78.44 | 78.76
5/20/2010 | 1:00:00 PM | 77.15 | 77.88 | 76.17 | 68.28 | 69.49 | 100 | 74.96 | 75.98 | 75.56 | 74.65 |  |  |  |  |  |  | 75.73 | 75.63 | 77.47 | 76.21 | 76.36 |  | 79.44 | 79.29 | 78.66 | 78.64 | 79.63
5/20/2010 | 2:00:00 PM | 77.15 | 78.5 | 76.73 | 68.28 | 69.59 | 100 | 74.96 | 77.04 | 76.74 | 75.35 |  |  |  |  |  |  | 78.07 | 77.76 | 78.92 | 77.97 | 77.72 |  | 79.97 | 80.6 | 79.65 | 79.34 | 80.82
5/20/2010 | 3:00:00 PM | 77.22 | 78.8 | 77.34 | 68.59 | 70.19 | 100 | 74.96 | 77.79 | 77.84 | 75.35 |  |  |  |  |  |  | 79.74 | 79.56 | 79.96 | 79.28 | 78.18 |  | 81.05 | 81.47 | 80.58 | 80.08 | 81.18
5/20/2010 | 4:00:00 PM | 77.93 | 78.08 | 78.26 | 68.97 | 69.87 | 100 | 74.96 | 77.02 | 77.18 | 75.35 |  |  |  |  |  |  | 81.24 | 80.92 | 80.11 | 79.29 | 78.18 |  | 81.74 | 81.47 | 80.77 | 80.08 | 81.18
5/21/2010 | 7:00:00 AM | 75.02 | 73.51 | 72.44 | 64.96 | 68.02 | 100 | 73.53 | 73.11 | 72.34 | 73.45 |  |  |  |  |  |  | 76.5 | 76.19 | 78.88 | 74.68 | 73.52 |  | 77.11 | 75.75 | 74.94 | 74.15 | 75.57
5/21/2010 | 8:00:00 AM | 74.81 | 73.72 | 72.8 | 66.06 | 68.02 | 100 | 73.67 | 73.49 | 72.75 | 74.46 |  |  |  |  |  |  | 76.09 | 76.2 | 78.51 | 74.59 | 74.82 |  | 78.08 | 76.61 | 75.88 | 76.23 | 77.35
5/21/2010 | 9:00:00 AM | 75.82 | 76.18 | 75.33 | 67.17 | 68.48 | 77.49 | 74.61 | 76.05 | 74.83 | 74.77 |  |  |  |  |  |  | 77.16 | 76.99 | 78.59 | 76.28 | 77.18 |  | 80.28 | 79.83 | 78.55 | 78.85 | 80.8
5/21/2010 | 10:00:00 AM | 77.47 | 77.45 | 76.48 | 68.7 | 68.71 | 77.49 | 75.26 | 77.04 | 75.9 | 74.77 |  |  |  |  |  |  | 77.99 | 78.24 | 79.38 | 77.26 | 78.63 |  | 81.4 | 81.98 | 80.35 | 80.51 | 81.47
5/21/2010 | 11:00:00 AM | 77.93 | 78.06 | 76.8 | 69.5 | 68.71 | 76.75 | 75.74 | 76.15 | 76.13 | 74.77 |  |  |  |  |  |  | 78.04 | 79.28 | 80.1 | 77.73 | 78.19 |  | 81.86 | 82.51 | 81.24 | 80.97 | 82.06
5/21/2010 | 12:00:00 PM | 77.93 | 77.7 | 76.58 | 69.5 | 68.71 | 76.57 | 75.08 | 74.12 | 75.58 | 74.49 |  |  |  |  |  |  | 78.04 | 79.25 | 80.1 | 77.54 | 76.46 |  | 81.3 | 81.34 | 80.07 | 79.21 | 80.53
5/21/2010 | 1:00:00 PM | 77.67 | 76.54 | 75.78 | 69.5 | 68.64 | 75.92 | 74.21 | 72.85 | 74.38 | 73.92 |  |  |  |  |  |  | 78.04 | 78.53 | 80.1 | 76.79 | 75.4 |  | 80.05 | 80.06 | 79.4 | 77.72 | 78.91
5/21/2010 | 2:00:00 PM | 77.07 | 76.29 | 75.24 | 68.92 | 68.48 | 75.92 | 73.68 | 73.26 | 73.72 | 73.92 |  |  |  |  |  |  | 78.04 | 78.53 | 80.1 | 76.79 | 74.69 |  | 79.24 | 79.97 | 78.82 | 77.65 | 78.67
5/21/2010 | 3:00:00 PM | 76.37 | 75.62 | 74.88 | 68.71 | 68.54 | 75.92 | 73.45 | 73.59 | 73.72 | 73.92 |  |  |  |  |  |  | 78.87 | 79.16 | 80.1 | 77.37 | 74.69 |  | 78.61 | 79.65 | 78.82 | 77.86 | 77.93
5/21/2010 | 4:00:00 PM | 76.37 | 75.62 | 74.48 | 68.71 | 68.8 | 75.92 | 73.45 | 73.59 | 73.72 | 73.92 |  |  |  |  |  |  | 80.7 | 81.01 | 80.1 | 78.68 | 75.22 |  | 79 | 79.14 | 78.82 | 78.44 | 77.93

## Slide 8: 2010: 5/24-5/28
5/24/2010 | 7:00:00 AM | 73.29 | 73.33 | 70.21 | 64.97 | 71.24 | 74.43 | 71.97 | 72.72 | 70.67 | 73.53 |  |  |  |  |  |  | 75.1 | 75.37 | 77.91 | 72.69 | 70.11 |  | 75.4 | 74.46 | 74.44 | 73.6 | 74.39
5/24/2010 | 8:00:00 AM | 73.29 | 73.38 | 70.28 | 65.04 | 71.24 | 74.39 | 71.97 | 72.89 | 70.82 | 74.13 |  |  |  |  |  |  | 74.97 | 75.39 | 76.96 | 72.24 | 70.67 |  | 75.63 | 74.72 | 74.71 | 74.07 | 74.62
5/24/2010 | 9:00:00 AM | 73.83 | 74.82 | 73.4 | 65.63 | 71.24 | 74.76 | 73.04 | 74.87 | 73.3 | 74.32 |  |  |  |  |  |  | 76.07 | 76.8 | 77.08 | 74.29 | 73.72 |  | 78.18 | 77.52 | 77.66 | 77.45 | 78.2
5/24/2010 | 10:00:00 AM | 75.29 | 76.59 | 75.03 | 65.63 | 71.52 | 75.22 | 73.76 | 76.84 | 75.16 | 74.32 |  |  |  |  |  |  | 77.15 | 78.16 | 78.56 | 75.93 | 76.36 |  | 80.46 | 79.99 | 79.72 | 79.28 | 80.57
5/24/2010 | 11:00:00 AM | 76.95 | 77.91 | 76.34 | 65.63 | 72.57 | 75.64 | 74.66 | 77.88 | 76.21 | 74.36 |  |  |  |  |  |  | 78.03 | 78.97 | 80.26 | 76.99 | 78.04 |  | 82.12 | 81.68 | 81.14 | 81.07 | 82.28
5/24/2010 | 12:00:00 PM | 77.92 | 79.01 | 77.25 | 66.44 | 73.87 | 76.67 | 74.92 | 78.18 | 77.31 | 75.08 |  |  |  |  |  |  | 78.8 | 79.32 | 80.88 | 77.72 | 79.7 |  | 83.72 | 82.22 | 81.42 | 81.68 | 82.87
5/24/2010 | 1:00:00 PM | 77.92 | 79.55 | 77.93 | 67.23 | 74.9 | 77.72 | 75.3 | 78.18 | 77.43 | 75.08 |  |  |  |  |  |  | 79.72 | 79.86 | 80.89 | 78.96 | 80.32 |  | 84.23 | 82.83 | 82.49 | 82.22 | 82.87
5/24/2010 | 2:00:00 PM | 77.92 | 78.77 | 78.51 | 68.33 | 75.74 | 77.72 | 76.33 | 79.04 | 78.12 | 75.08 |  |  |  |  |  |  | 80.52 | 81.27 | 81.69 | 79.47 | 81.35 |  | 84.23 | 83.08 | 82.79 | 82.62 | 83.48
5/24/2010 | 3:00:00 PM | 78.59 | 78.69 | 78.51 | 68.36 | 76.48 | 78.52 | 76.43 | 79.71 | 78.83 | 75.22 |  |  |  |  |  |  | 82.12 | 82.41 | 82.04 | 80.93 | 81.74 |  | 84.23 | 83.08 | 82.79 | 83.05 | 83.72
5/24/2010 | 4:00:00 PM | 78.71 | 78.69 | 78.51 | 68.36 | 77.16 | 79.37 | 76.43 | 78.89 | 79.01 | 75.87 |  |  |  |  |  |  | 83.41 | 83.59 | 82.52 | 81.83 | 81.74 |  | 84.23 | 83.08 | 83.54 | 83.05 | 83.72
5/25/2010 | 7:00:00 AM | 74.79 | 74.31 | 73.25 | 67.67 | 74.15 | 75.59 | 74.94 | 74.29 | 72.84 | 73.41 |  |  |  |  |  |  | 77.59 | 77.69 | 79.8 | 75.95 | 74.71 |  | 78.26 | 76.62 | 72.63 | 74.19 | 75.74
5/25/2010 | 8:00:00 AM | 74.82 | 74.23 | 73.43 | 68.16 | 74.15 | 75.39 | 76.04 | 74.63 | 73.33 | 74.21 |  |  |  |  |  |  | 77.31 | 77.09 | 79.18 | 75.79 | 76.39 |  | 78.79 | 77.35 | 74.5 | 76.15 | 77.27
5/25/2010 | 9:00:00 AM | 76.16 | 76.31 | 75.46 | 69.19 | 74.15 | 75.82 | 77.8 | 77.2 | 75.84 | 74.85 |  |  |  |  |  |  | 77.93 | 77.58 | 79.18 | 77.38 | 79.46 |  | 81.69 | 80.02 | 77.8 | 78.78 | 80
5/25/2010 | 10:00:00 AM | 77.58 | 78.45 | 78.02 | 70.07 | 74.36 | 76.86 | 79.02 | 79.31 | 77.76 | 76.08 |  |  |  |  |  |  | 79.26 | 78.89 | 80.25 | 78.99 | 80.88 |  | 83.88 | 82.12 | 80.36 | 80.37 | 82.9
5/25/2010 | 11:00:00 AM | 78.96 | 80.57 | 79.61 | 71.47 | 75.34 | 77.29 | 79.87 | 80.31 | 78.97 | 76.08 |  |  |  |  |  |  | 80.21 | 79.97 | 81.48 | 79.93 | 82.33 |  | 85.5 | 83.8 | 81.91 | 82.25 | 84.65
5/25/2010 | 12:00:00 PM | 79.99 | 81.14 | 80.71 | 72.65 | 76.55 | 78.28 | 80.62 | 80.68 | 80.2 | 76.72 |  |  |  |  |  |  | 81.82 | 80.91 | 82.45 | 80.23 | 83.92 |  | 86.54 | 84.88 | 82.92 | 83.16 | 85.42
5/25/2010 | 1:00:00 PM | 80.28 | 80.82 | 80.93 | 73.37 | 77.28 | 79.65 | 81.26 | 81.27 | 80.6 | 76.98 |  |  |  |  |  |  | 82.53 | 82.02 | 82.98 | 82.43 | 84.69 |  | 86.78 | 85.14 | 84.23 | 83.76 | 85.93
5/25/2010 | 2:00:00 PM | 80.39 | 80.86 | 81.33 | 73.69 | 78.58 | 80.6 | 82.07 | 82.09 | 81.7 | 77.65 |  |  |  |  |  |  | 83.54 | 83.45 | 84.26 | 83.6 | 85.57 |  | 87.47 | 85.73 | 84.55 | 84.52 | 86.48
5/25/2010 | 3:00:00 PM | 81.09 | 81.02 | 82.35 | 73.77 | 80.16 | 81.31 | 82.94 | 82.36 | 81.48 | 77.65 |  |  |  |  |  |  | 85.75 | 84.64 | 85.02 | 84.76 | 85.86 |  | 87.66 | 85.73 | 85.26 | 84.76 | 86.48
5/25/2010 | 4:00:00 PM | 81.09 | 81.02 | 82.61 | 73.77 | 81.06 | 81.82 | 82.97 | 81.62 | 81.37 | 77.65 |  |  |  |  |  |  | 89.02 | 87.67 | 85.02 | 85.64 | 85.86 |  | 87.66 | 85.73 | 85.26 | 85.52 | 86.48
5/26/2010 | 7:00:00 AM | 76.6 | 77.18 | 76.25 | 72.47 | 77.51 | 77.46 | 79.67 | 77.41 | 75.75 | 75.39 |  |  |  |  |  |  | 79.32 | 79.48 | 80.74 | 78.26 | 78.78 |  | 79.96 | 79.82 | 79.33 | 78.31 | 79.36
5/26/2010 | 8:00:00 AM | 76.74 | 77.17 | 76.71 | 71.36 | 77.15 | 78.02 | 79.67 | 77.57 | 76.58 | 75.27 |  |  |  |  |  |  | 79.3 | 79.42 | 80.87 | 78.56 | 79.88 |  | 80.9 | 80.5 | 79.68 | 80.52 | 80.64
5/26/2010 | 9:00:00 AM | 79.01 | 79.43 | 79.67 | 72.83 | 77.72 | 78.61 | 79.67 | 79.48 | 79.19 | 76.5 |  |  |  |  |  |  | 80.7 | 81.25 | 81.99 | 80.49 | 82.89 |  | 83.77 | 83.62 | 82.01 | 82.8 | 84.51
5/26/2010 | 10:00:00 AM | 80.71 | 81.48 | 82.32 | 73.92 | 78.72 | 79.81 | 79.67 | 81.39 | 81 | 77.73 |  |  |  |  |  |  | 82.45 | 83.53 | 83.28 | 82.51 | 85.06 |  | 85.98 | 85.07 | 84.28 | 84.35 | 86.66
5/26/2010 | 11:00:00 AM | 81.99 | 82.48 | 83.9 | 74.96 | 79.31 | 81.78 | 80.26 | 82.47 | 82.39 | 78.48 |  |  |  |  |  |  | 83.66 | 84.24 | 84.52 | 84.24 | 85.91 |  | 87.82 | 86.21 | 85.43 | 85.68 | 88.04
5/26/2010 | 12:00:00 PM | 83.06 | 82.79 | 84.19 | 75.78 | 80.22 | 83.7 | 80.47 | 83.07 | 83.59 | 79.55 |  |  |  |  |  |  | 84.91 | 84.34 | 85.48 | 85.15 | 86.65 |  | 88.61 | 87.35 | 86.44 | 86.69 | 88.45
5/26/2010 | 1:00:00 PM | 83.61 | 82.8 | 84.19 | 75.8 | 81.21 | 84.74 | 80.63 | 83.3 | 84.03 | 80.21 |  |  |  |  |  |  | 86.38 | 85.54 | 86.08 | 86.26 | 87.7 |  | 89.22 | 88.19 | 87.56 | 88.09 | 88.96
5/26/2010 | 2:00:00 PM | 83.81 | 83.63 | 84.69 | 76.53 | 81.95 | 85.31 | 81.31 | 83.94 | 84.25 | 80.66 |  |  |  |  |  |  | 88.06 | 87.11 | 87.29 | 86.73 | 88.54 |  | 90.11 | 89.09 | 87.94 | 88.65 | 89.42
5/26/2010 | 3:00:00 PM | 84.46 | 83.63 | 85.05 | 76.53 | 82.62 | 85.31 | 81.31 | 86.45 | 85.7 | 80.66 |  |  |  |  |  |  | 89.44 | 88.62 | 88.13 | 87.33 | 89.01 |  | 90.42 | 89.33 | 88.42 | 88.65 | 89.86
5/26/2010 | 4:00:00 PM | 84.46 | 83.63 | 85.49 | 76.53 | 83.24 | 85.31 | 81.31 | 85.47 | 85.76 | 81.27 |  |  |  |  |  |  | 93.23 | 91.56 | 88.4 | 88.51 | 89.63 |  | 90.7 | 89.33 | 89.43 | 88.77 | 89.86
5/27/2010 | 7:00:00 AM | 77.25 | 77.94 | 76.04 | 69.65 | 78.5 | 79.31 | 80.48 | 77.64 | 74.61 | 74 |  |  |  |  |  |  | 77.93 | 79.04 | 81.41 | 77.08 | 77.14 |  | 78.87 | 78.57 | 78.7 | 77.55 | 77.8
5/27/2010 | 8:00:00 AM | 76.16 | 76.25 | 74.82 | 69.65 | 77.76 | 77.95 | 78.88 | 77.01 | 69.81 | 73.6 |  |  |  |  |  |  | 76.83 | 78.63 | 80.79 | 77.1 | 76.06 |  | 78.23 | 77.95 | 78.53 | 76.63 | 76.24
5/27/2010 | 9:00:00 AM | 76.64 | 76.78 | 74.76 | 69.71 | 77.76 | 77.68 | 75.7 | 76.32 | 69.95 | 73.9 |  |  |  |  |  |  | 79.13 | 80.14 | 80.5 | 78.45 | 76.51 |  | 79.53 | 79.27 | 80.23 | 78.17 | 78.28
5/27/2010 | 10:00:00 AM | 77.04 | 77 | 75.27 | 70.32 | 78.19 | 76.93 | 76.79 | 76.44 | 71.23 | 73.93 |  |  |  |  |  |  | 79.23 | 80.69 | 81.3 | 79 | 77.7 |  | 80.43 | 80.4 | 81.79 | 78.7 | 79.3
5/27/2010 | 11:00:00 AM | 77.64 | 77.87 | 76.19 | 69.64 | 78.54 | 75.49 | 78.72 | 77.89 | 72.87 | 74.65 |  |  |  |  |  |  | 79.23 | 81.08 | 81.94 | 79.24 | 78.97 |  | 81.51 | 81.3 | 81.3 | 80.09 | 80.58
5/27/2010 | 12:00:00 PM | 78.12 | 78.51 | 77.73 | 70.19 | 79.11 | 74.77 | 78.37 | 78.24 | 74.47 | 74.65 |  |  |  |  |  |  | 79.23 | 80.83 | 82.15 | 79.45 | 79.57 |  | 82.75 | 82.04 | 81.18 | 80.69 | 81.18
5/27/2010 | 1:00:00 PM | 78.48 | 77.82 | 78.66 | 71.07 | 80.15 | 75.73 | 78.76 | 78.24 | 75.21 | 74.65 |  |  |  |  |  |  | 80.93 | 81.63 | 82.15 | 80.4 | 79.33 |  | 83.08 | 82.35 | 81.62 | 80.88 | 81.18
5/27/2010 | 2:00:00 PM | 79.23 | 77.82 | 78.82 | 71.07 | 80.15 | 76.31 | 79.97 | 78.92 | 75.8 | 75.25 |  |  |  |  |  |  | 81.01 | 82.11 | 82.93 | 81 | 80.07 |  | 83.69 | 82.87 | 82 | 81.94 | 82.4
5/27/2010 | 3:00:00 PM | 79.23 | 78.6 | 79.47 | 71.07 | 80.15 | 76.91 | 81.71 | 79.67 | 75.97 | 75.43 |  |  |  |  |  |  | 81.74 | 82.52 | 83.01 | 80.36 | 80.71 |  | 83.41 | 83.45 | 82.74 | 82.36 | 82.84
5/27/2010 | 4:00:00 PM | 78.96 | 78.18 | 79.47 | 71.38 | 80.66 | 76.91 | 82.72 | 79.2 | 75.97 | 75.18 |  |  |  |  |  |  | 82.84 | 83.6 | 83.58 | 81.61 | 80.11 |  | 83.07 | 83.72 | 82.83 | 81.92 | 82.84
5/28/2010 | 7:00:00 AM | 75.01 | 75.51 | 72.6 | 66.58 | 72.89 | 76.19 | 78.65 | 74.37 | 70.84 | 73.75 |  |  |  |  |  |  | 75.48 | 76.32 | 80.31 | 73.22 | 74.09 |  | 77.09 | 75.2 | 75.87 | 74.26 | 74.66
5/28/2010 | 8:00:00 AM | 74.44 | 74.66 | 72.81 | 66.03 | 72.89 | 75.64 | 78.65 | 74.62 | 70.76 | 74.11 |  |  |  |  |  |  | 74.7 | 75.68 | 78.57 | 72.44 | 75.12 |  | 78.02 | 75.83 | 75.97 | 75.3 | 76.04
5/28/2010 | 9:00:00 AM | 75.48 | 76.75 | 75.42 | 66.75 | 72.92 | 75.41 | 79.22 | 76.89 | 73.37 | 74.55 |  |  |  |  |  |  | 75.76 | 76.54 | 78.48 | 73.93 | 77.67 |  | 80.9 | 78.93 | 78.68 | 78.49 | 78.57
5/28/2010 | 10:00:00 AM | 77.06 | 78.32 | 76.83 | 67.87 | 73.62 | 74.51 | 76.38 | 78.28 | 74.92 | 75.08 |  |  |  |  |  |  | 76.71 | 77.72 | 79.27 | 75.67 | 79.43 |  | 82.19 | 80.62 | 80.82 | 79.51 | 80.11
5/28/2010 | 11:00:00 AM | 78.42 | 78.92 | 77.61 | 69.69 | 73.62 | 74.72 | 75.25 | 79.14 | 75.77 | 75.34 |  |  |  |  |  |  | 77.07 | 78.38 | 80.51 | 76.07 | 80.33 |  | 83.17 | 82.16 | 81.8 | 80.66 | 81.46
5/28/2010 | 12:00:00 PM | 79.13 | 79.29 | 78.44 | 70.88 | 73.88 | 75.34 | 74.57 | 79.86 | 76.24 | 75.34 |  |  |  |  |  |  | 78.16 | 78.8 | 81.23 | 77 | 80.14 |  | 83.77 | 83.11 | 81.8 | 81.35 | 81.69
5/28/2010 | 1:00:00 PM | 79.13 | 78.63 | 78.65 | 70.83 | 74.61 | 75.95 | 75 | 79.86 | 76.53 | 75.34 |  |  |  |  |  |  | 78.83 | 79.09 | 81.26 | 78.04 | 79.57 |  | 83.77 | 83.11 | 82.67 | 81.35 | 81.69
5/28/2010 | 2:00:00 PM | 79.13 | 77.49 | 78.57 | 70.32 | 76.41 | 76.12 | 75.07 | 79.86 | 76.53 | 75.34 |  |  |  |  |  |  | 79.61 | 80.29 | 82.05 | 78.39 | 80.35 |  | 84.36 | 83.11 | 82.21 | 81.35 | 82.38
5/28/2010 | 3:00:00 PM | 79.13 | 76.89 | 77.92 | 69.88 | 76.7 | 76.12 | 75.33 | 79.86 | 76.23 | 75.34 |  |  |  |  |  |  | 80.95 | 80.84 | 82.77 | 79.13 | 79.51 |  | 83.86 | 82.91 | 81.85 | 81.35 | 81.64
5/28/2010 | 4:00:00 PM | 78.45 | 76.39 | 77.31 | 69.76 | 76.7 | 76.12 | 75.68 | 79.52 | 75.36 | 75 |  |  |  |  |  |  | 81.76 | 82.33 | 82.88 | 79.64 | 78.8 |  | 82.67 | 81.76 | 81.01 | 80.5 | 80.69

## Slide 9: 2010: 6/1-6/4
6/1/2010 | 7:00:00 AM |  |  |  |  |  | 77.3 | 75.84 | 75 | 73.73 | 73.81 |  |  |  |  |  |  | 77.33 | 76.48 | 79.5 | 76.11 | 74.92 |  | 78.25 | 77.79 | 76.9 | 76.1 | 76.77
6/1/2010 | 8:00:00 AM |  |  |  |  |  | 77 | 76.13 | 75 | 72.75 | 73.81 |  |  |  |  |  |  | 76.51 | 76.08 | 78.75 | 75.72 | 75.03 |  | 77.89 | 77.15 | 76.93 | 76.17 | 76.55
6/1/2010 | 9:00:00 AM |  |  |  |  |  | 77 | 77.24 | 76.12 | 74.35 | 74.29 |  |  |  |  |  |  | 77.56 | 77.29 | 78.7 | 76.64 | 76.03 |  | 79.34 | 78.73 | 78.58 | 78.56 | 78.34
6/1/2010 | 10:00:00 AM | 75.46 | 76.86 | 75.4 | 68.99 | 73.35 | 77 | 78.39 | 77.48 | 75.64 | 74.58 |  |  |  |  |  |  | 78.55 | 78.49 | 79.45 | 78.57 | 76.45 |  | 80.42 | 79.97 | 80.23 | 79.42 | 79.02
6/1/2010 | 11:00:00 AM | 76.87 | 78.03 | 76.73 | 69.26 | 73.35 | 77.23 | 79.5 | 78.66 | 77.16 | 74.69 |  |  |  |  |  |  | 79.82 | 80.06 | 80.75 | 79.64 | 77.84 |  | 81.72 | 81.78 | 81.44 | 80.82 | 81.04
6/1/2010 | 12:00:00 PM | 78.23 | 79.02 | 78.78 | 70.55 | 73.35 | 78.77 | 79.97 | 79.4 | 78.28 | 76.07 |  |  |  |  |  |  | 81.03 | 80.83 | 81.94 | 80.09 | 80.23 |  | 83.33 | 83 | 82.11 | 81.7 | 82.06
6/1/2010 | 1:00:00 PM | 79.07 | 79.02 | 79.19 | 71.57 | 73.46 | 79.44 | 80.7 | 79.87 | 78.72 | 76.62 |  |  |  |  |  |  | 81.74 | 81.62 | 82 | 81.8 | 82 |  | 84.06 | 84.06 | 83.63 | 82.74 | 82.06
6/1/2010 | 2:00:00 PM | 79.62 | 79.02 | 80.35 | 72.13 | 75.26 | 80.54 | 81.44 | 80.91 | 79.93 | 77.31 |  |  |  |  |  |  | 82.68 | 82.53 | 83.16 | 82.54 | 83.34 |  | 85.14 | 84.54 | 84.19 | 83.28 | 82.47
6/1/2010 | 3:00:00 PM | 79.62 | 79.02 | 81.35 | 73.28 | 76.18 | 81.2 | 81.98 | 81.33 | 80.13 | 77.77 |  |  |  |  |  |  | 83.22 | 83.44 | 83.6 | 82.98 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 83.74
6/1/2010 | 4:00:00 PM | 79.62 | 78.9 | 80.24 | 73.3 | 77.11 | 80.78 | 82.56 | 81.33 | 79.81 | 77.62 |  |  |  |  |  |  | 83.06 | 83.08 | 83.6 | 82.2 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 83.22
6/2/2010 | 7:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 8:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 9:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 10:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 11:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 12:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 1:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 2:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 3:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/2/2010 | 4:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 7:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 8:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 9:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 10:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 11:00:00 AM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 12:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 1:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 2:00:00 PM | 79.62 | 78.21 | 79.14 | 73.3 | 77.16 | 80.39 | 83.11 | 81.33 | 79.29 | 76.96 |  |  |  |  |  |  | 82.36 | 82.61 | 83.6 | 81.06 | 83.92 |  | 85.22 | 84.54 | 84.86 | 83.28 | 82.01
6/3/2010 | 3:00:00 PM | 79.82 | 78.66 | 79.49 | 73.31 | 76.79 | 80.44 | 83.18 | 81.59 | 79.42 | 76.67 |  |  |  |  |  |  | 82.54 | 82.83 | 83.79 | 81.51 | 83.99 |  | 85.39 | 84.66 | 82.84 | 83.39 | 82.34
6/3/2010 | 4:00:00 PM | 80.66 | 80.51 | 80.93 | 73.33 | 74.64 | 80.7 | 83.46 | 82.72 | 80.01 | 75.38 |  |  |  |  |  |  | 84.03 | 84.9 | 85.47 | 85.62 | 84.63 |  | 87.31 | 86.03 | 85.08 | 84.61 | 86.18
6/4/2010 | 7:00:00 AM | 76.74 | 76.73 | 76.27 | 71.87 | 75.14 | 79.07 | 80.43 | 76.6 | 74.2 | 73.92 |  |  |  |  |  |  | 77.64 | 78.32 | 81.97 | 77.16 | 76.74 |  | 79.66 | 79.18 | 79.11 | 77.16 | 78.1
6/4/2010 | 8:00:00 AM | 75.8 | 75.68 | 75.29 | 71.87 | 75.14 | 78.45 | 79.62 | 76.41 | 73.53 | 74.04 |  |  |  |  |  |  | 76.79 | 78.15 | 81.21 | 76.38 | 76.34 |  | 79.37 | 78.91 | 78.68 | 77.06 | 77.29
6/4/2010 | 9:00:00 AM | 75.8 | 76.94 | 75.77 | 71.87 | 75.14 | 78.24 | 79.36 | 77.7 | 74.02 | 74.22 |  |  |  |  |  |  | 78.19 | 78.29 | 81.15 | 78.21 | 78.78 |  | 79.37 | 79.16 | 78.68 | 76.98 | 78.55
6/4/2010 | 10:00:00 AM | 75.96 | 77.52 | 76.11 | 72.05 | 75.14 | 78.24 | 79.36 | 78.35 | 75.42 | 74.22 |  |  |  |  |  |  | 79.03 | 79.75 | 81.55 | 80.39 | 80.1 |  | 80.25 | 80.38 | 78.92 | 77.83 | 78.96
6/4/2010 | 11:00:00 AM | 77.71 | 78.89 | 78.03 | 72.91 | 75.14 | 78.24 | 79.36 | 79.62 | 77.5 | 74.22 |  |  |  |  |  |  | 80.07 | 81.31 | 83.18 | 81.33 | 82.51 |  | 82.88 | 81.93 | 80.5 | 80.64 | 81.57
6/4/2010 | 12:00:00 PM | 78.93 | 79.92 | 79.16 | 73.31 | 75.14 | 78.36 | 79.36 | 80.32 | 78.22 | 74.71 |  |  |  |  |  |  | 81.22 | 81.4 | 83.65 | 82.03 | 84.01 |  | 84.88 | 83.1 | 81.75 | 81 | 82.69
6/4/2010 | 1:00:00 PM | 79.04 | 80.56 | 79.91 | 73.31 | 75.14 | 79.04 | 80.1 | 80.5 | 78.94 | 74.99 |  |  |  |  |  |  | 82.13 | 82.16 | 83.65 | 84.23 | 84.47 |  | 85.19 | 83.85 | 82.75 | 82.26 | 82.78
6/4/2010 | 2:00:00 PM | 79.84 | 80.56 | 80.76 | 73.31 | 75.14 | 79.74 | 80.15 | 81.14 | 79.82 | 74.99 |  |  |  |  |  |  | 82.82 | 83.82 | 84.45 | 84.71 | 85.8 |  | 85.19 | 84.64 | 83.76 | 83.48 | 84.09
6/4/2010 | 3:00:00 PM | 80.61 | 80.56 | 80.76 | 73.31 | 75.14 | 80.49 | 80.15 | 81.91 | 80.34 | 74.99 |  |  |  |  |  |  | 84.94 | 84.91 | 85.13 | 85.56 | 85.32 |  | 85.19 | 85.35 | 84.56 | 83.48 | 84.36
6/4/2010 | 4:00:00 PM | 80.61 | 80.56 | 80.76 | 73.31 | 75.14 | 80.79 | 80.15 | 81.73 | 80.51 | 74.99 |  |  |  |  |  |  | 87.31 | 86.73 | 85.37 | 85.84 | 85.32 |  | 85.88 | 85.56 | 85.27 | 83.48 | 84.36
6/4/2010 | 5:00:00 PM | 80.61 | 79.94 | 80.76 | 73.31 | 75.14 | 81.47 | 80.88 | 81.15 | 79.8 | 74.52 |  |  |  |  |  |  | 87.95 | 88.27 | 86.03 | 86.5 | 85.32 |  | 86.05 | 85.56 | 85.72 | 83.48 | 84.36

## Slide 10: 2010: 6/7-6/11
6/7/2010 | 8:00:00 AM | 74.72 | 75.03 | 74.13 | 68.55 | 73.74 | 75.42 | 75.92 | 74.1 | 70.72 | 75.34 |  |  |  |  |  |  | 76.73 | 74.16 | 78.01 | 73.62 | 75.13 |  | 78.69 | 78.34 | 78.2 | 78.06 | 78.46
6/7/2010 | 9:00:00 AM | 75.96 | 76.85 | 75.48 | 68.55 | 73.73 | 74.31 | 76.68 | 76.05 | 72.08 | 75.43 |  |  |  |  |  |  | 77.85 | 74.64 | 78.37 | 75.32 | 76.21 |  | 81.15 | 80.91 | 80.56 | 80.76 | 81.37
6/7/2010 | 10:00:00 AM | 76.83 | 78.36 | 77.54 | 69.09 | 73.73 | 71.8 | 76.79 | 77.09 | 73.95 | 75.43 |  |  |  |  |  |  | 78.61 | 75.92 | 79.14 | 75.04 | 77.12 |  | 82.9 | 82.51 | 82.32 | 82.05 | 83.1
6/7/2010 | 11:00:00 AM | 77.32 | 78.95 | 78.63 | 69.9 | 74.43 | 72.77 | 76.03 | 77.97 | 75.21 | 75.43 |  |  |  |  |  |  | 77.22 | 76.5 | 79.97 | 75.99 | 78.13 |  | 84.09 | 83.83 | 83.34 | 83.09 | 84.19
6/7/2010 | 12:00:00 PM | 77.73 | 78.95 | 79.29 | 70.79 | 75.15 | 74.61 | 75.04 | 78.35 | 76.26 | 75.43 |  |  |  |  |  |  | 76.97 | 76.78 | 80.41 | 76.17 | 79.37 |  | 85 | 84.39 | 83.34 | 83.92 | 84.8
6/7/2010 | 1:00:00 PM | 77.73 | 78.95 | 79.5 | 70.85 | 75.23 | 75.37 | 74.8 | 78.35 | 76.5 | 76.17 |  |  |  |  |  |  | 77.35 | 76.99 | 80.42 | 77.08 | 80 |  | 85.44 | 84.39 | 84.11 | 83.92 | 85.2
6/7/2010 | 2:00:00 PM | 78.08 | 78.38 | 79.28 | 71.14 | 75.23 | 75.15 | 75.09 | 78.97 | 77.14 | 76.09 |  |  |  |  |  |  | 77.86 | 78.05 | 81.42 | 77.04 | 80 |  | 85.44 | 84.39 | 84.18 | 83.92 | 85.2
6/7/2010 | 3:00:00 PM | 78.52 | 78.13 | 78.71 | 71.58 | 75.23 | 74.74 | 76 | 79.41 | 77.29 | 75.39 |  |  |  |  |  |  | 78.42 | 78.67 | 82.04 | 77.09 | 80 |  | 85.44 | 84.39 | 84.18 | 83.92 | 85.2
6/7/2010 | 4:00:00 PM | 78.52 | 78.13 | 78.71 | 71.45 | 74.61 | 75.41 | 76.23 | 78.79 | 77.29 | 75.39 |  |  |  |  |  |  | 79.72 | 80.13 | 82.04 | 77.01 | 80 |  | 84.65 | 84.39 | 84.13 | 83.29 | 85.2
6/8/2010 | 7:00:00 AM | 73.59 | 73.22 | 71.47 | 63.94 | 73.65 | 74.84 | 74.69 | 72.25 | 70.38 | 71.13 |  |  |  |  |  |  | 72.11 | 72.84 | 77.53 | 69.94 | 70.87 |  | 75.33 | 75.01 | 74.26 | 73.19 | 74.25
6/8/2010 | 8:00:00 AM | 74.47 | 74.35 | 73.38 | 65.28 | 73.65 | 74.45 | 74.98 | 73.05 | 71.11 | 72.3 |  |  |  |  |  |  | 73.92 | 73.41 | 77.16 | 71.76 | 73.55 |  | 77.67 | 77.09 | 76.74 | 76.65 | 77.15
6/8/2010 | 9:00:00 AM | 76.29 | 75 | 74.78 | 67.57 | 73.65 | 72.57 | 75.88 | 75.64 | 73.41 | 74.15 |  |  |  |  |  |  | 75.8 | 74.41 | 77.39 | 73.77 | 76.37 |  | 80.5 | 80.13 | 80.01 | 79.96 | 80.54
6/8/2010 | 10:00:00 AM | 76.94 | 76.47 | 76.13 | 68.48 | 73.65 | 73.5 | 76.29 | 77.33 | 74.77 | 74.18 |  |  |  |  |  |  | 77.6 | 75.59 | 78.21 | 74.88 | 77.45 |  | 82.34 | 81.96 | 82.2 | 81.03 | 82.23
6/8/2010 | 11:00:00 AM | 77.5 | 77.56 | 76.76 | 69.1 | 74.29 | 74.1 | 76.29 | 78.31 | 75.55 | 74.18 |  |  |  |  |  |  | 77.85 | 77.14 | 79.06 | 74.8 | 78.3 |  | 83.64 | 83.3 | 83.17 | 82.18 | 83.26
6/8/2010 | 12:00:00 PM | 77.5 | 77.56 | 76.41 | 69.17 | 75.11 | 74.24 | 76.29 | 78.36 | 76.41 | 74.18 |  |  |  |  |  |  | 78.39 | 76.52 | 79.51 | 74.39 | 78.31 |  | 84.26 | 84.03 | 83.17 | 82.21 | 83.29
6/8/2010 | 1:00:00 PM | 77.5 | 76.48 | 75.98 | 69.17 | 74.83 | 72.68 | 76.29 | 78.36 | 76.41 | 74.18 |  |  |  |  |  |  | 78.99 | 77.22 | 79.51 | 75.96 | 78.31 |  | 84.26 | 84.03 | 83.17 | 82.21 | 83.29
6/8/2010 | 2:00:00 PM | 77.89 | 76.21 | 76.63 | 69.17 | 75.02 | 72.7 | 76.99 | 78.77 | 76.84 | 74.4 |  |  |  |  |  |  | 79.11 | 78.72 | 80.2 | 75.79 | 78.43 |  | 84.26 | 84.03 | 83.17 | 82.21 | 83.29
6/8/2010 | 3:00:00 PM | 78.29 | 75.72 | 76.76 | 68.9 | 75.03 | 72.86 | 75.72 | 79.09 | 77.22 | 74.92 |  |  |  |  |  |  | 78.53 | 79.72 | 80.44 | 75.79 | 79.11 |  | 84.26 | 84.03 | 83.17 | 82.21 | 83.29
6/8/2010 | 4:00:00 PM | 78.29 | 75.41 | 76.27 | 68.45 | 75.02 | 73.2 | 74.58 | 78.21 | 76.06 | 74.92 |  |  |  |  |  |  | 79.81 | 80.23 | 81.11 | 76.34 | 79.11 |  | 84.26 | 84.03 | 82.72 | 82.21 | 83.29
6/9/2010 | 7:00:00 AM | 72.47 | 72.92 | 68.11 | 62.3 | 73.17 | 72.9 | 73.91 | 72.03 | 67.01 | 73.26 |  |  |  |  |  |  | 70.46 | 73.29 | 75.93 | 70.16 | 68.74 |  | 73.48 | 73.19 | 72.56 | 70.86 | 71.74
6/9/2010 | 8:00:00 AM | 72.31 | 71.83 | 68.94 | 63.59 | 73.17 | 72.3 | 74.34 | 72.35 | 67.66 | 73.72 |  |  |  |  |  |  | 71.03 | 73.03 | 75.27 | 70.57 | 70.49 |  | 74.49 | 74.34 | 73.52 | 72.67 | 72.94
6/9/2010 | 9:00:00 AM | 74.11 | 73.89 | 70.92 | 64.7 | 73.17 | 72.15 | 74.51 | 73.98 | 70.13 | 73.73 |  |  |  |  |  |  | 72.95 | 74.48 | 75.61 | 72.04 | 72.5 |  | 76.85 | 77.07 | 76.47 | 75.93 | 76.05
6/9/2010 | 10:00:00 AM | 75.08 | 74.85 | 72.05 | 66.2 | 73.77 | 72.15 | 75.43 | 74.27 | 71.72 | 74.06 |  |  |  |  |  |  | 73.27 | 75.58 | 75.8 | 72.92 | 73.04 |  | 77.58 | 78.29 | 77.13 | 76.36 | 76.3
6/9/2010 | 11:00:00 AM | 75.66 | 75.9 | 72.91 | 67.29 | 73.91 | 72.42 | 76.59 | 74.27 | 72.69 | 74.06 |  |  |  |  |  |  | 73.32 | 76.59 | 77.04 | 74.16 | 74.27 |  | 78.88 | 78.78 | 77.77 | 77.73 | 77.66
6/9/2010 | 12:00:00 PM | 76.58 | 76.83 | 74.85 | 68.69 | 74.14 | 73.04 | 77.12 | 74.27 | 73.44 | 74.74 |  |  |  |  |  |  | 74.4 | 77.58 | 78.27 | 75.29 | 75.4 |  | 79.99 | 79.96 | 78.93 | 78.8 | 78.61
6/9/2010 | 1:00:00 PM | 76.52 | 76.32 | 76.09 | 69.52 | 74.82 | 73.23 | 77.67 | 75.04 | 73.95 | 74.8 |  |  |  |  |  |  | 76.32 | 78.81 | 78.73 | 77.2 | 76.65 |  | 80.98 | 81.35 | 80.33 | 80.18 | 78.61
6/9/2010 | 2:00:00 PM | 76.35 | 76.06 | 76.27 | 69.52 | 75.41 | 73.47 | 78.41 | 75.82 | 74.95 | 74.8 |  |  |  |  |  |  | 77.52 | 79.61 | 79.94 | 78.04 | 77.89 |  | 82.18 | 81.85 | 80.93 | 80.6 | 79.66
6/9/2010 | 3:00:00 PM | 75.78 | 76.43 | 76.86 | 69.52 | 74.39 | 73.07 | 78.46 | 75.82 | 74.69 | 74.8 |  |  |  |  |  |  | 78.76 | 79.9 | 81.03 | 78.04 | 77.61 |  | 82.48 | 81.56 | 80.93 | 80.99 | 80.93
6/9/2010 | 4:00:00 PM | 75.59 | 76.83 | 76.78 | 69.41 | 73.86 | 72.76 | 78.46 | 75.29 | 73.27 | 74.8 |  |  |  |  |  |  | 78.54 | 79.59 | 81.15 | 77.26 | 76.51 |  | 82.48 | 81.03 | 80.14 | 80.66 | 81.03
6/10/2010 | 7:00:00 AM | 71.28 | 71.13 | 70.18 | 62.7 | 71.4 | 72.48 | 75.35 | 71.19 | 68.14 | 73.42 |  |  |  |  |  |  | 71.28 | 70.8 | 75.17 | 70.44 | 69.45 |  | 73.78 | 73.19 | 72.34 | 70.62 | 71.61
6/10/2010 | 8:00:00 AM | 70.57 | 70.47 | 69.17 | 63.31 | 71.4 | 71.48 | 74.6 | 70.61 | 68.01 | 73.28 |  |  |  |  |  |  | 70.35 | 70.01 | 74.35 | 70.44 | 68.88 |  | 72.77 | 72.66 | 71.62 | 70.15 | 70.69
6/10/2010 | 9:00:00 AM | 70.14 | 71.28 | 70.05 | 63.53 | 71.42 | 71.23 | 74.59 | 70.41 | 70.18 | 73.6 |  |  |  |  |  |  | 70.97 | 71.12 | 74.66 | 70.69 | 69.47 |  | 73.36 | 74.31 | 72.85 | 71.69 | 72.29
6/10/2010 | 10:00:00 AM | 70.14 | 72.08 | 70.4 | 63.95 | 72.12 | 71.23 | 74.59 | 70.59 | 70.22 | 73.6 |  |  |  |  |  |  | 71.29 | 71.92 | 74.73 | 71.18 | 69.17 |  | 73.88 | 74.89 | 72.67 | 71.79 | 72.75
6/10/2010 | 11:00:00 AM | 70.73 | 72.31 | 70.21 | 64.49 | 72.77 | 71.23 | 74.59 | 71.13 | 70.22 | 73.6 |  |  |  |  |  |  | 70.33 | 72.84 | 75.14 | 71.91 | 70.42 |  | 74.02 | 74.02 | 72.84 | 72.67 | 72.92
6/10/2010 | 12:00:00 PM | 70.87 | 71.9 | 71.04 | 65.06 | 73.5 | 71.81 | 74.83 | 71.13 | 70.56 | 73.76 |  |  |  |  |  |  | 70.33 | 72.23 | 75.49 | 70.78 | 70.9 |  | 74.15 | 73.9 | 72.65 | 72.17 | 73.32
6/10/2010 | 1:00:00 PM | 70.87 | 71.9 | 71.37 | 65.93 | 73.61 | 71.99 | 75.34 | 72.08 | 70.82 | 73.53 |  |  |  |  |  |  | 71.49 | 72.29 | 75.49 | 71.42 | 72.14 |  | 74.65 | 74.79 | 73.54 | 72.4 | 72.97
6/10/2010 | 2:00:00 PM | 71.47 | 71.34 | 71.88 | 66.39 | 74.18 | 71.99 | 75.34 | 72.64 | 71.13 | 73.65 |  |  |  |  |  |  | 71.5 | 73.54 | 75.49 | 70.77 | 73.06 |  | 75.56 | 74.72 | 73.41 | 73.2 | 73.63
6/10/2010 | 3:00:00 PM | 71.59 | 71.12 | 72.16 | 66.62 | 73.86 | 71.99 | 75.34 | 72.64 | 70.42 | 73.74 |  |  |  |  |  |  | 73.15 | 73.59 | 75.49 | 71.65 | 72.84 |  | 75.27 | 75.17 | 72.79 | 73.13 | 72.86
6/10/2010 | 4:00:00 PM | 71.38 | 70.42 | 70.88 | 66.62 | 73.66 | 71.99 | 74.74 | 71.92 | 70.42 | 73.61 |  |  |  |  |  |  | 72.65 | 73.59 | 75.49 | 71.65 | 71.89 |  | 74.89 | 74.76 | 72.79 | 71.71 | 72.78
6/11/2010 | 7:00:00 AM | 70.34 | 70.12 | 69.08 | 61.97 | 70.58 | 71.34 | 73.08 | 69.73 | 67.86 | 73.4 |  |  |  |  |  |  | 70.03 | 69.35 | 73.05 | 69.44 | 67.98 |  | 71.55 | 70.99 | 70.41 | 69.01 | 70.34
6/11/2010 | 8:00:00 AM | 69.62 | 69.59 | 68.15 | 62.44 | 70.58 | 70.64 | 73.17 | 69.56 | 67.85 | 73.4 |  |  |  |  |  |  | 69.45 | 69.31 | 72.49 | 69.44 | 67.58 |  | 71.13 | 70.42 | 70 | 68.65 | 69.51
6/11/2010 | 9:00:00 AM | 69.86 | 70.5 | 68.21 | 62.6 | 70.79 | 70.54 | 73.82 | 69.56 | 69.43 | 73.4 |  |  |  |  |  |  | 71.72 | 71.19 | 72.88 | 70.45 | 69.21 |  | 72.2 | 72.11 | 71.14 | 70.81 | 70.15
6/11/2010 | 10:00:00 AM | 70.08 | 71.25 | 69.31 | 63.15 | 71.3 | 70.54 | 74.3 | 70.68 | 70.23 | 73.4 |  |  |  |  |  |  | 71.12 | 72.4 | 73.23 | 70.51 | 69.45 |  | 72.61 | 72.43 | 71.53 | 71.46 | 72.87
6/11/2010 | 11:00:00 AM | 71.09 | 71.93 | 69.54 | 63.41 | 71.85 | 70.54 | 75.49 | 72.31 | 71.05 | 73.67 |  |  |  |  |  |  | 70.71 | 73.39 | 74.26 | 70.94 | 70.1 |  | 73.48 | 73.09 | 72.65 | 72.81 | 74.25
6/11/2010 | 12:00:00 PM | 71.55 | 72.5 | 70.45 | 64.19 | 72.54 | 70.54 | 76.43 | 72.87 | 71.43 | 74.23 |  |  |  |  |  |  | 71.06 | 73.1 | 74.79 | 70.74 | 70.86 |  | 74.1 | 73.22 | 72.79 | 72.85 | 74.67
6/11/2010 | 1:00:00 PM | 71.55 | 71.83 | 71.35 | 64.55 | 72.75 | 70.54 | 77 | 73.67 | 71.56 | 74.23 |  |  |  |  |  |  | 73.2 | 74.22 | 74.79 | 71.93 | 71.74 |  | 74.47 | 74.35 | 73.77 | 74.26 | 75.72
6/11/2010 | 2:00:00 PM | 71.91 | 71.83 | 71.89 | 65.38 | 72.85 | 70.94 | 78.14 | 74.04 | 72.36 | 74.23 |  |  |  |  |  |  | 73.68 | 74.22 | 75.77 | 72.23 | 72.98 |  | 75.79 | 74.58 | 74.22 | 74.68 | 76.96
6/11/2010 | 3:00:00 PM | 72.29 | 71.83 | 72.98 | 66.41 | 73.49 | 71.25 | 78.44 | 73.32 | 72 | 74.14 |  |  |  |  |  |  | 74.05 | 74.54 | 76.32 | 72.13 | 73.58 |  | 76.38 | 75.16 | 74.66 | 74.72 | 77.92
6/11/2010 | 4:00:00 PM | 72.29 | 71.69 | 71.76 | 66.54 | 73.49 | 71.25 | 78.44 | 72.82 | 71.62 | 74.08 |  |  |  |  |  |  | 73.76 | 74.24 | 76.32 | 71.42 | 73.04 |  | 76.38 | 74.72 | 73.9 | 74.29 | 77.6

## Slide 11: 2010: 6/14-6/18
6/14/2010 | 7:00:00 AM | 70.07 | 69.56 | 68.76 | 62.55 | 70.56 | 71.57 | 71.92 | 70.47 | 69.2 | 73.47 |  |  |  |  |  |  | 71.61 | 70.32 | 72.33 | 68.79 | 68.27 |  | 71.47 | 70.86 | 70.59 | 70.55 | 73.4
6/14/2010 | 8:00:00 AM | 70.07 | 69.56 | 68.19 | 62.67 | 70.55 | 71.94 | 71.57 | 70.52 | 69.1 | 73.58 |  |  |  |  |  |  | 71.35 | 70.32 | 71.82 | 68.92 | 68.14 |  | 71.15 | 70.62 | 70.69 | 70.8 | 73.4
6/14/2010 | 9:00:00 AM | 70.86 | 70.35 | 69.74 | 63.64 | 71.29 | 71.94 | 71.57 | 71.79 | 71.05 | 73.92 |  |  |  |  |  |  | 72.02 | 71.63 | 72.49 | 70.68 | 69.82 |  | 72.42 | 72.52 | 72.25 | 72.35 | 74.6
6/14/2010 | 10:00:00 AM | 71.51 | 71.16 | 70.17 | 64.39 | 72.02 | 71.94 | 71.63 | 73.08 | 71.6 | 74.22 |  |  |  |  |  |  | 73.1 | 73.26 | 73.5 | 71.23 | 71.16 |  | 73.49 | 73.67 | 73.5 | 73.02 | 75.63
6/14/2010 | 11:00:00 AM | 71.51 | 71.85 | 70.91 | 65.06 | 72.39 | 71.94 | 72.29 | 74.14 | 72.38 | 74.22 |  |  |  |  |  |  | 73.11 | 73.99 | 74.4 | 71.98 | 72.33 |  | 74.51 | 74.51 | 74.05 | 74.52 | 76.4
6/14/2010 | 12:00:00 PM | 71.72 | 72.47 | 72.08 | 65.78 | 73.23 | 71.94 | 72.29 | 74.77 | 72.97 | 74.22 |  |  |  |  |  |  | 73.92 | 73.46 | 74.77 | 73.73 | 73.37 |  | 75.87 | 74.7 | 74.19 | 74.55 | 76.4
6/14/2010 | 1:00:00 PM | 72.24 | 73.17 | 73.31 | 66 | 74.25 | 72.39 | 73.02 | 74.77 | 73.24 | 74.22 |  |  |  |  |  |  | 74.98 | 74.23 | 74.95 | 74.78 | 74.34 |  | 76.53 | 75.71 | 75.5 | 76.38 | 77.17
6/14/2010 | 2:00:00 PM | 72.95 | 73.21 | 73.94 | 66.94 | 74.28 | 73.22 | 73.56 | 75.21 | 74.45 | 74.22 |  |  |  |  |  |  | 75.8 | 76.08 | 76.09 | 75.45 | 75.5 |  | 78.19 | 77.1 | 76.56 | 77.93 | 78.76
6/14/2010 | 3:00:00 PM | 73.6 | 73.56 | 73.94 | 67.12 | 75.33 | 73.83 | 73.77 | 75.61 | 75.04 | 74.22 |  |  |  |  |  |  | 76.46 | 76.97 | 76.81 | 76.2 | 76.89 |  | 78.58 | 77.88 | 77.79 | 78.82 | 78.93
6/14/2010 | 4:00:00 PM | 74.12 | 73.95 | 74.55 | 67.12 | 75.07 | 74.21 | 73.77 | 75.28 | 75.21 | 74.22 |  |  |  |  |  |  | 78.03 | 77.6 | 77.15 | 76.65 | 77.14 |  | 78.58 | 78.56 | 78.45 | 78.82 | 78.93
6/15/2010 | 7:00:00 AM | 70.6 | 70.07 | 69.52 | 63.71 | 73.07 | 73.08 | 73.02 | 72.04 | 68.65 | 73.45 |  |  |  |  |  |  | 73.03 | 72.72 | 75.48 | 71.61 | 71.05 |  | 73.84 | 72.72 | 72.61 | 71.58 | 76.56
6/15/2010 | 8:00:00 AM | 71.04 | 70.92 | 70.59 | 64.58 | 72.5 | 73.39 | 73.77 | 72 | 70.02 | 74.19 |  |  |  |  |  |  | 73.57 | 72.94 | 74.72 | 71.9 | 72.99 |  | 75.23 | 75.11 | 74.51 | 74.85 | 76.74
6/15/2010 | 9:00:00 AM | 72.09 | 72.32 | 72.25 | 66.06 | 72.5 | 73.39 | 75.32 | 73.83 | 71.92 | 74.7 |  |  |  |  |  |  | 75.07 | 74.81 | 75.35 | 73.44 | 75.12 |  | 78.22 | 78.54 | 78.41 | 79 | 79.23
6/15/2010 | 10:00:00 AM | 73.33 | 73.97 | 73.77 | 67.26 | 72.69 | 73.39 | 76.37 | 75.32 | 73.11 | 73.99 |  |  |  |  |  |  | 76.13 | 76.84 | 76.42 | 74.84 | 76.57 |  | 80.14 | 80.8 | 80.45 | 80.82 | 80.43
6/15/2010 | 11:00:00 AM | 74.27 | 74.87 | 74.6 | 67.93 | 73.23 | 74.05 | 77.28 | 76.57 | 74.1 | 73.94 |  |  |  |  |  |  | 77.13 | 77.55 | 77.36 | 75.84 | 77.74 |  | 81.42 | 81.86 | 81.08 | 81.46 | 81.69
6/15/2010 | 12:00:00 PM | 75.01 | 75.26 | 74.6 | 68.42 | 73.66 | 74.12 | 77.96 | 77.26 | 75.26 | 73.94 |  |  |  |  |  |  | 77.64 | 78.12 | 77.79 | 76.93 | 78.46 |  | 82.88 | 82.47 | 81.68 | 81.46 | 82.4
6/15/2010 | 1:00:00 PM | 75.01 | 75.26 | 74.6 | 68.5 | 73.97 | 74.85 | 79.03 | 77.26 | 75.74 | 73.94 |  |  |  |  |  |  | 78.26 | 78.9 | 78.19 | 77.68 | 79.14 |  | 83.48 | 83.53 | 82.73 | 82.29 | 82.4
6/15/2010 | 2:00:00 PM | 75.11 | 75.93 | 74.6 | 69.11 | 74.37 | 74.87 | 80.09 | 77.26 | 76.41 | 73.94 |  |  |  |  |  |  | 79.06 | 79.76 | 79.39 | 78 | 79.6 |  | 83.48 | 83.77 | 82.76 | 82.48 | 82.4
6/15/2010 | 3:00:00 PM | 75.78 | 76.03 | 74.6 | 69.24 | 74.72 | 75.24 | 80.09 | 78.01 | 76.5 | 73.94 |  |  |  |  |  |  | 80.5 | 80.82 | 80.18 | 79.14 | 80.3 |  | 83.48 | 83.77 | 82.76 | 82.25 | 82.4
6/15/2010 | 4:00:00 PM | 75.78 | 76.03 | 75.33 | 69.81 | 74.72 | 76.18 | 80.09 | 77.41 | 76.5 | 73.94 |  |  |  |  |  |  | 81.36 | 81.8 | 80.18 | 79.3 | 80.47 |  | 83.48 | 83.77 | 82.76 | 82.25 | 82.4
6/16/2010 | 7:00:00 AM | 71.11 | 71.03 | 69.7 | 63.93 | 73.22 | 74.17 | 76.12 | 73.52 | 68.94 | 72.88 |  |  |  |  |  |  | 73.14 | 74.58 | 77.53 | 71.5 | 71.16 |  | 74.62 | 75.04 | 74.09 | 72.64 | 78.29
6/16/2010 | 8:00:00 AM | 71.19 | 71.25 | 69.8 | 63.08 | 73.21 | 74.17 | 76.12 | 73.61 | 69.67 | 73.7 |  |  |  |  |  |  | 73.4 | 74.54 | 76.94 | 71.86 | 71.85 |  | 75.28 | 75.58 | 74.76 | 74.04 | 78.35
6/16/2010 | 9:00:00 AM | 73.5 | 73.98 | 72.84 | 64.53 | 73.9 | 74.17 | 76.12 | 74.79 | 71.73 | 74.41 |  |  |  |  |  |  | 76.4 | 76.32 | 76.94 | 74.86 | 74.51 |  | 78.49 | 78.94 | 78.04 | 78.01 | 79.96
6/16/2010 | 10:00:00 AM | 74.88 | 75.59 | 74.73 | 65.81 | 75.16 | 74.17 | 76.12 | 75.06 | 72.51 | 74.41 |  |  |  |  |  |  | 77.42 | 77.59 | 77.34 | 76.75 | 74.7 |  | 79.81 | 80.12 | 78.82 | 78.8 | 80.17
6/16/2010 | 11:00:00 AM | 75.72 | 76.53 | 75.18 | 67.11 | 75.47 | 74.82 | 76.12 | 75.06 | 73.55 | 74.41 |  |  |  |  |  |  | 77.6 | 78.73 | 78.69 | 78.26 | 75.76 |  | 81.08 | 80.59 | 80.05 | 79.41 | 81.59
6/16/2010 | 12:00:00 PM | 75.72 | 76.53 | 75.18 | 67.9 | 75.47 | 75.06 | 76.21 | 75.06 | 74.91 | 74.41 |  |  |  |  |  |  | 77.6 | 78.8 | 79.31 | 78.56 | 76.56 |  | 81.76 | 81.16 | 80.43 | 80.07 | 82.22
6/16/2010 | 1:00:00 PM | 75.72 | 76.53 | 75.18 | 68.46 | 75.47 | 75.79 | 76.9 | 75.41 | 75.61 | 74.41 |  |  |  |  |  |  | 78.7 | 79.2 | 79.47 | 79.95 | 78.26 |  | 82.56 | 82.61 | 81.85 | 81.04 | 81.99
6/16/2010 | 2:00:00 PM | 75.72 | 76.08 | 75.18 | 69.08 | 75.47 | 77.2 | 76.9 | 76.9 | 76.1 | 74.11 |  |  |  |  |  |  | 79.46 | 80.38 | 80.68 | 80.79 | 80.01 |  | 83.42 | 83.13 | 82.5 | 81.04 | 83.21
6/16/2010 | 3:00:00 PM | 75.72 | 75.77 | 75.27 | 69.08 | 74.82 | 77.25 | 76.9 | 77.4 | 75.41 | 73.62 |  |  |  |  |  |  | 80.05 | 80.45 | 80.93 | 81.45 | 79.79 |  | 83.42 | 83.13 | 82.5 | 81.86 | 82.43
6/16/2010 | 4:00:00 PM | 76.34 | 75.77 | 75.93 | 69.08 | 74.66 | 77.25 | 76.9 | 77.1 | 75.41 | 73.62 |  |  |  |  |  |  | 80.05 | 80.45 | 80.93 | 80.92 | 79.46 |  | 83.63 | 83.13 | 82.5 | 81.86 | 82.43
6/17/2010 | 7:00:00 AM | 74.18 | 74.22 | 74.41 | 67.13 | 74.66 | 77 | 76.11 | 75.05 | 74.56 | 73.75 |  |  |  |  |  |  | 75.68 | 76.5 | 78.98 | 76.12 | 76.27 |  | 79.31 | 77.94 | 77.62 | 76.87 | 78.21
6/17/2010 | 8:00:00 AM | 74.18 | 74.4 | 74.58 | 68.03 | 74.66 | 77 | 76.11 | 75.17 | 74.84 | 73.86 |  |  |  |  |  |  | 76.51 | 76.8 | 78.51 | 77.14 | 77.11 |  | 80.5 | 79.18 | 78.75 | 78.62 | 79.18
6/17/2010 | 9:00:00 AM | 74.43 | 74.97 | 75.17 | 68.61 | 74.66 | 76.75 | 76.8 | 75.9 | 75.36 | 74.12 |  |  |  |  |  |  | 78.07 | 76.91 | 78.85 | 79.94 | 79.76 |  | 81.73 | 81.14 | 80.61 | 80.63 | 80.62
6/17/2010 | 10:00:00 AM | 74.93 | 74.97 | 75.17 | 68.31 | 73.54 | 74.41 | 76.34 | 76.68 | 75.49 | 74.12 |  |  |  |  |  |  | 78.93 | 74.79 | 79.87 | 78.88 | 80.31 |  | 81.73 | 81.27 | 81.51 | 80.7 | 81.3
6/17/2010 | 11:00:00 AM | 75.47 | 74.97 | 75.17 | 68.75 | 72.82 | 74.41 | 76.1 | 77.42 | 76.12 | 74.12 |  |  |  |  |  |  | 78.48 | 74.71 | 80.09 | 78.47 | 79.63 |  | 82.19 | 81.27 | 81.51 | 80.88 | 81.3
6/17/2010 | 12:00:00 PM | 75.68 | 74.97 | 75.47 | 69.47 | 72.82 | 74.15 | 76.1 | 77.42 | 76.3 | 74.12 |  |  |  |  |  |  | 78.07 | 74.95 | 80.09 | 78.47 | 79.86 |  | 83.24 | 81.27 | 81.51 | 81.6 | 81.3
6/17/2010 | 1:00:00 PM | 75.68 | 74.97 | 75.94 | 69.72 | 72.82 | 74.97 | 76.1 | 77.18 | 76.89 | 74.12 |  |  |  |  |  |  | 78.39 | 75.46 | 80.09 | 78.47 | 80 |  | 83.34 | 82.1 | 82.31 | 81.6 | 81.3
6/17/2010 | 2:00:00 PM | 75.68 | 75.32 | 75.94 | 69.72 | 72.82 | 75.92 | 76.1 | 77.06 | 76.89 | 74.12 |  |  |  |  |  |  | 78.86 | 76.32 | 80.09 | 78.47 | 79.48 |  | 82.58 | 82.88 | 82.33 | 81.6 | 81.61
6/17/2010 | 3:00:00 PM | 75.68 | 75.72 | 75.94 | 69.72 | 72.82 | 76.22 | 76.1 | 77.68 | 76.89 | 74.12 |  |  |  |  |  |  | 78.68 | 77 | 80.09 | 78.47 | 79.48 |  | 82.58 | 82.93 | 82.33 | 81.6 | 82.13
6/17/2010 | 4:00:00 PM | 75.68 | 75.72 | 75.94 | 69.72 | 72.82 | 76.22 | 76.1 | 76.59 | 76.78 | 74.12 |  |  |  |  |  |  | 78.07 | 76.71 | 80.09 | 78.78 | 79.48 |  | 82.58 | 82.93 | 82.33 | 81.6 | 82.13
6/18/2010 | 7:00:00 AM | 71.15 | 71.93 | 71.57 | 65.56 | 72.82 | 73.61 | 74.57 | 73.65 | 70.39 | 73.52 |  |  |  |  |  |  | 70.24 | 71.72 | 76.14 | 71.49 | 71.18 |  | 73.58 | 73.29 | 74.37 | 71.99 | 77.21
6/18/2010 | 8:00:00 AM | 72.09 | 72.77 | 72.45 | 66.09 | 72.82 | 73.89 | 74.57 | 73.77 | 71.71 | 74.45 |  |  |  |  |  |  | 71.34 | 72.48 | 76.1 | 72.64 | 73.45 |  | 75.28 | 75.31 | 75.52 | 74.9 | 77.69
6/18/2010 | 9:00:00 AM | 73.4 | 74.58 | 74.91 | 67.41 | 72.82 | 74.22 | 75.15 | 75.23 | 74.73 | 74.68 |  |  |  |  |  |  | 72.24 | 74.87 | 76.61 | 75.44 | 77.58 |  | 78.64 | 80.41 | 79.03 | 78.71 | 79.72
6/18/2010 | 10:00:00 AM | 74.26 | 76.08 | 76.25 | 68.93 | 72.82 | 75.21 | 75.33 | 75.98 | 75.91 | 74.12 |  |  |  |  |  |  | 72.97 | 76.16 | 77.65 | 77.2 | 79.22 |  | 80.62 | 83.94 | 82.12 | 80.49 | 81.8
6/18/2010 | 11:00:00 AM | 74.64 | 77 | 77.05 | 70.22 | 72.82 | 76.45 | 75.33 | 75.98 | 75.91 | 73.93 |  |  |  |  |  |  | 73.63 | 76.16 | 77.65 | 78.47 | 80.64 |  | 81.78 | 84.11 | 83.22 | 81.36 | 83.18
6/18/2010 | 12:00:00 PM | 75.28 | 77.17 | 77.96 | 70.74 | 72.87 | 78.01 | 75.99 | 75.98 | 75.91 | 74.2 |  |  |  |  |  |  | 74.6 | 76.55 | 77.71 | 77.82 | 80.74 |  | 82.35 | 84.11 | 83.22 | 82 | 83.18
6/18/2010 | 1:00:00 PM | 75.39 | 77.17 | 77.98 | 71.1 | 72.78 | 78.67 | 77.56 | 76.01 | 75.91 | 74.72 |  |  |  |  |  |  | 75.57 | 77.71 | 78.43 | 78.81 | 80.74 |  | 82.56 | 84.11 | 83.22 | 82.19 | 82.44
6/18/2010 | 2:00:00 PM | 75.39 | 77.17 | 77.98 | 71.1 | 72.78 | 78.22 | 78.62 | 76.75 | 75.91 | 74.58 |  |  |  |  |  |  | 76.45 | 78.77 | 78.86 | 79.93 | 81.41 |  | 83.18 | 84.11 | 83.54 | 82.19 | 82.31
6/18/2010 | 3:00:00 PM | 75.39 | 77.17 | 77.98 | 71.1 | 72.9 | 78.22 | 78.56 | 76.75 | 75.91 | 73.97 |  |  |  |  |  |  | 78.21 | 81.6 | 79.98 | 81.5 | 81.6 |  | 83.18 | 84.23 | 84.05 | 82.9 | 82.31
6/18/2010 | 4:00:00 PM | 75.39 | 77.17 | 77.98 | 71.1 | 73.53 | 78.22 | 77.83 | 76.81 | 76.04 | 73.97 |  |  |  |  |  |  | 80.59 | 84.25 | 80.76 | 83.03 | 82.43 |  | 83.82 | 84.97 | 84.05 | 83.03 | 82.39

## Slide 12: 2010: 6/21-6/23
6/21/2010 | 7:00:00 AM | 76.91 | 77.93 | 78.15 | 70.25 | 73.26 | 80.11 | 77.81 | 77.52 | 78.25 | 78.93 |  |  |  |  |  |  | 83.62 | 83.78 | 83.82 | 81.94 | 82.08 |  | 84.88 | 83.15 | 83.96 | 83.81 | 84.77
6/21/2010 | 8:00:00 AM | 76.98 | 78.02 | 78.71 | 70.95 | 73.22 | 80.4 | 78.05 | 77.51 | 78.34 | 77.66 |  |  |  |  |  |  | 83.12 | 83 | 83.19 | 81.75 | 82.66 |  | 85.11 | 83.83 | 84.19 | 84.31 | 84.96
6/21/2010 | 9:00:00 AM | 77.48 | 78.33 | 79.89 | 72.06 | 72.77 | 80.56 | 79.23 | 77.47 | 78.73 | 77.75 |  |  |  |  |  |  | 82.99 | 82.86 | 82.99 | 81.43 | 83.24 |  | 86.62 | 85.86 | 85.87 | 85.96 | 86.31
6/21/2010 | 10:00:00 AM | 77.98 | 79.11 | 80.73 | 72.81 | 72.77 | 79.88 | 79.55 | 77.84 | 79.47 | 77.75 |  |  |  |  |  |  | 82.99 | 83.53 | 82.99 | 81.43 | 83.54 |  | 87.68 | 87.22 | 87.22 | 87.14 | 87.69
6/21/2010 | 11:00:00 AM | 78.27 | 79.11 | 81.1 | 73.53 | 72.77 | 80.17 | 79.55 | 78.25 | 79.47 | 77.49 |  |  |  |  |  |  | 83.01 | 83.83 | 82.99 | 81.43 | 84.54 |  | 88.4 | 88.15 | 88.3 | 88.05 | 88.25
6/21/2010 | 12:00:00 PM | 78.77 | 79.11 | 81.1 | 73.47 | 72.77 | 80.7 | 79.55 | 78.25 | 79.47 | 76.97 |  |  |  |  |  |  | 84 | 83.83 | 82.99 | 81.53 | 85.47 |  | 88.98 | 88.31 | 88.3 | 88.12 | 88.97
6/21/2010 | 1:00:00 PM | 78.77 | 79.11 | 81.1 | 73.16 | 72.77 | 81.58 | 79.55 | 78.25 | 79.47 | 76.97 |  |  |  |  |  |  | 84.49 | 83.99 | 83.26 | 82.66 | 85.47 |  | 89.29 | 88.31 | 88.3 | 88.12 | 89.13
6/21/2010 | 2:00:00 PM | 78.77 | 79.11 | 81.1 | 73.79 | 72.77 | 81.6 | 79.55 | 78.61 | 79.47 | 76.97 |  |  |  |  |  |  | 85.21 | 84.79 | 84.08 | 83.37 | 85.65 |  | 89.29 | 88.31 | 88.3 | 88.12 | 89.13
6/21/2010 | 3:00:00 PM | 78.77 | 79.11 | 81.1 | 73.37 | 72.77 | 82.26 | 79.55 | 79.06 | 79.47 | 76.26 |  |  |  |  |  |  | 86.42 | 86.01 | 84.62 | 84.15 | 86.36 |  | 89.29 | 88.31 | 88.3 | 88.12 | 89.13
6/21/2010 | 4:00:00 PM | 78.77 | 79.11 | 81.1 | 73.68 | 72.77 | 83.05 | 79.55 | 79.06 | 79.47 | 76.18 |  |  |  |  |  |  | 88.16 | 87.46 | 84.94 | 84.88 | 86.36 |  | 89.29 | 88.31 | 88.3 | 88.12 | 89.13
6/22/2010 | 7:00:00 AM | 77.2 | 78.74 | 78.87 | 70.71 | 75 | 80.3 | 78.75 | 78.26 | 78.66 | 77.74 |  |  |  |  |  |  | 84.21 | 83.76 | 84.05 | 81.85 | 82.03 |  | 85.95 | 83.94 | 84.16 | 83.76 | 84.75
6/22/2010 | 8:00:00 AM | 77.2 | 78.32 | 78.68 | 70.71 | 75 | 74.35 | 78.75 | 78.26 | 78.66 | 76.04 |  |  |  |  |  |  | 83.97 | 83.76 | 84.05 | 81.76 | 82.81 |  | 85.37 | 83.19 | 83.94 | 83.76 | 84.75
6/22/2010 | 9:00:00 AM | 77.2 | 78.32 | 78.68 | 71.08 | 75 | 76.13 | 78.75 | 75.43 | 78.66 | 75.19 |  |  |  |  |  |  | 83.97 | 83.76 | 84.05 | 81.76 | 82.86 |  | 85.58 | 81.08 | 83.94 | 83.76 | 84.75
6/22/2010 | 10:00:00 AM | 77.2 | 78.32 | 79.27 | 71.44 | 75 | 76.89 | 78.75 | 75.73 | 78.66 | 75.19 |  |  |  |  |  |  | 83.97 | 83.76 | 84.05 | 81.76 | 81.51 |  | 85.76 | 82.97 | 83.94 | 84.43 | 84.75
6/22/2010 | 11:00:00 AM | 77.21 | 78.57 | 79.68 | 72.17 | 75 | 78.23 | 78.75 | 77.75 | 78.66 | 75.19 |  |  |  |  |  |  | 83.97 | 83.76 | 84.05 | 82.17 | 81.31 |  | 86.83 | 85.17 | 84.51 | 85.06 | 85.22
6/22/2010 | 12:00:00 PM | 77.97 | 79.11 | 80.28 | 72.9 | 75.71 | 79.35 | 78.75 | 79.26 | 78.66 | 75.19 |  |  |  |  |  |  | 84.3 | 83.76 | 84.05 | 82.68 | 82.39 |  | 87.42 | 86.46 | 85.65 | 85.48 | 85.6
6/22/2010 | 1:00:00 PM | 77.97 | 79.11 | 80.28 | 73.29 | 75.85 | 80.54 | 78.75 | 80.08 | 78.66 | 75.66 |  |  |  |  |  |  | 84.81 | 84.15 | 84.05 | 83.7 | 83.1 |  | 87.42 | 86.51 | 86.41 | 85.48 | 85.6
6/22/2010 | 2:00:00 PM | 77.97 | 79.11 | 80.28 | 73.65 | 76.53 | 80.54 | 78.75 | 81.11 | 78.66 | 75.97 |  |  |  |  |  |  | 85.72 | 85 | 84.19 | 84.66 | 83.58 |  | 87.42 | 86.73 | 86.52 | 85.57 | 85.6
6/22/2010 | 3:00:00 PM | 77.97 | 79.11 | 80.28 | 73.65 | 77.1 | 82.2 | 78.75 | 81.43 | 78.69 | 75.97 |  |  |  |  |  |  | 86.95 | 86.15 | 84.9 | 85.45 | 84.32 |  | 87.94 | 87.56 | 87.24 | 86.7 | 86.36
6/22/2010 | 4:00:00 PM | 77.97 | 79.11 | 80.28 | 73.65 | 77.57 | 82.88 | 78.75 | 81.07 | 79.47 | 75.96 |  |  |  |  |  |  | 88.19 | 87.22 | 85.56 | 85.99 | 84.42 |  | 88.29 | 88.26 | 87.4 | 87.22 | 86.46
6/23/2010 | 7:00:00 AM | 77.97 | 79.11 | 80.28 | 72.15 | 77.3 | 80.67 | 78.72 | 78.49 | 79.23 | 77.2 |  |  |  |  |  |  | 83.9 | 83.27 | 84.48 | 82.59 | 82.71 |  | 86.51 | 84.77 | 84.26 | 84.61 | 83.86
6/23/2010 | 8:00:00 AM | 77.97 | 79.11 | 80.28 | 72.15 | 77.3 | 80.67 | 78.72 | 78.15 | 78.67 | 75.74 |  |  |  |  |  |  | 83.9 | 82.9 | 84.03 | 82.59 | 82.71 |  | 85.99 | 84.14 | 83.94 | 83.81 | 83.86
6/23/2010 | 9:00:00 AM | 77.97 | 79.11 | 80.28 | 72.4 | 77.3 | 80.67 | 78.72 | 78.15 | 78.67 | 75.69 |  |  |  |  |  |  | 83.9 | 82.9 | 84.03 | 82.59 | 82.83 |  | 85.84 | 84.32 | 83.94 | 84.42 | 84
6/23/2010 | 10:00:00 AM | 77.97 | 79.11 | 80.64 | 72.99 | 77.3 | 80.67 | 78.72 | 78.15 | 78.67 | 75.69 |  |  |  |  |  |  | 83.9 | 82.9 | 84.03 | 82.59 | 84.15 |  | 87.08 | 86.32 | 84.58 | 85.45 | 85.14
6/23/2010 | 11:00:00 AM | 77.97 | 79.11 | 81.09 | 71.26 | 77.3 | 80.67 | 79.2 | 78.15 | 78.67 | 75.69 |  |  |  |  |  |  | 83.9 | 82.9 | 84.03 | 82.59 | 84.4 |  | 87.38 | 87.37 | 85.42 | 86.16 | 85.58
6/23/2010 | 12:00:00 PM | 77.97 | 79.11 | 81.09 | 71.26 | 77.3 | 80.67 | 79.51 | 78.15 | 78.73 | 75.69 |  |  |  |  |  |  | 84.24 | 83.05 | 84.03 | 82.59 | 84.97 |  | 88.12 | 87.37 | 85.65 | 86.34 | 85.58
6/23/2010 | 1:00:00 PM | 77.97 | 79.11 | 81.09 | 71.26 | 77.99 | 81.2 | 79.51 | 78.15 | 79.46 | 75.69 |  |  |  |  |  |  | 84.75 | 83.73 | 84.03 | 82.59 | 85.26 |  | 88.26 | 87.37 | 85.65 | 86.34 | 85.58
6/23/2010 | 2:00:00 PM | 77.97 | 79.11 | 81.09 | 71.26 | 78.07 | 81.51 | 79.51 | 78.62 | 79.46 | 75.69 |  |  |  |  |  |  | 85.16 | 83.96 | 84.06 | 83.28 | 85.26 |  | 88.26 | 87.37 | 85.65 | 86.34 | 85.58
6/23/2010 | 3:00:00 PM | 77.97 | 79.11 | 81.09 | 71.26 | 78.26 | 81.83 | 79.51 | 78.93 | 79.46 | 75.69 |  |  |  |  |  |  | 86.14 | 84.88 | 84.88 | 84.43 | 85.81 |  | 88.26 | 87.37 | 86.39 | 86.34 | 85.68
6/23/2010 | 4:00:00 PM | 77.97 | 79.91 | 81.09 | 71.26 | 78.85 | 82.43 | 79.51 | 78.93 | 79.46 | 75.69 |  |  |  |  |  |  | 87.57 | 86.17 | 84.88 | 85.48 | 86.11 |  | 88.26 | 87.73 | 86.51 | 86.34 | 86.44

## Slide 13: 2010: 9/1-9/2
9/1/2010 | ######## | 80.19 | 79.77 | 79.98 | 70.86 | 77.78 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 80.19 | 79.73 | 79.98 | 70.97 | 77.78 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 81.04 | 80.9 | 81.39 | 71.63 | 77.78 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 82.18 | 82.59 | 83.05 | 71.63 | 77.78 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 82.67 | 83.58 | 83.33 | 71.63 | 77.95 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 83.39 | 84.11 | 84.11 | 72.09 | 83.06 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 83.5 | 84.59 | 84.19 | 72.35 | 81.77 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 84.21 | 85.1 | 84.25 | 72.35 | 81.31 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 84.44 | 85.47 | 85.04 | 72.35 | 81.31 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/1/2010 | ######## | 84.44 | 85.47 | 85.04 | 71.82 | 78.66 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 81.93 | 81.93 | 82.48 | 73.23 | 80.56 | 84.16 | 81.07 | 81.67 | 82.5 | 84.92 | 86.97 | 86.32 | 87.26 | 88.56 | 91.94 | 92.3 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 81.93 | 81.93 | 82.48 | 72.24 | 77.79 | 84.74 | 81.07 | 81.09 | 78.92 | 83.58 | 86.04 | 84.85 | 86.54 | 87.66 | 91.15 | 90.5 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 81.93 | 82.12 | 83.65 | 72.12 | 77.3 | 84.89 | 81.07 | 83.1 | 81.1 | 84.19 | 86.68 | 86.83 | 86.4 | 87.01 | 90.61 | 89.49 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 82.56 | 83.34 | 84.2 | 72.6 | 77.3 | 85.63 | 81.79 | 84.89 | 83.02 | 85.37 | 88.38 | 88.23 | 87.01 | 87.48 | 90.03 | 89.49 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 83.3 | 84.18 | 85.41 | 73.08 | 77.36 | 85.91 | 81.89 | 85.75 | 84.1 | 86.23 | 89.31 | 89.46 | 88.41 | 88.16 | 90.79 | 90.36 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 83.94 | 84.48 | 85.91 | 73.08 | 78.45 | 86.79 | 82.53 | 86.07 | 84.7 | 86.91 | 89.53 | 90.39 | 89.46 | 89.06 | 91.29 | 91.15 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 85.04 | 84.53 | 86.16 | 73.41 | 78.93 | 87.3 | 82.76 | 86.42 | 85.48 | 86.74 | 90.14 | 90.75 | 90.5 | 89.92 | 91.98 | 91.54 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 85.32 | 85.34 | 86.79 | 74.21 | 78.93 | 87.79 | 83.35 | 86.94 | 86 | 84.49 | 90.43 | 90.75 | 91.83 | 90.68 | 92.91 | 92.95 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 85.32 | 85.34 | 86.79 | 74.58 | 78.93 | 88.39 | 83.61 | 86.94 | 86 | 83.07 | 91.15 | 91.47 | 92.23 | 91.65 | 93.78 | 93.92 |  |  |  |  |  |  |  |  |  |  | 
9/2/2010 | ######## | 85.32 | 85.34 | 86.79 | 73.85 | 77.29 | 89.35 | 83.61 | 86.94 | 86 | 82.17 | 91.36 | 91.65 | 92.84 | 92.88 | 94.71 | 95.36 |  |  |  |  |  |  |  |  |  |  | 

## Slide 14: 2010: 9/7-9/10
9/7/2010 | ######## | 79.37 | 78.99 | 78.15 | 73.26 | 77.11 | 78.25 | 75.93 | 75.44 | 76.46 | 73.8 | 79.45 | 78.04 | 78.33 | 79.38 | 82.08 | 82.8 | 80.53 | 80.29 | 79.42 | 76.92 | 75.37 | 77.62 | 80.08 | 79.46 | 79.27 | 77.97 | 73.75
9/7/2010 | ######## | 79.37 | 78.62 | 78.02 | 71.36 | 77.14 | 78.49 | 75.93 | 74.85 | 73.62 | 73.66 | 78.87 | 77.04 | 77.68 | 78.4 | 81.75 | 81.86 | 79.85 | 79.7 | 79.42 | 76.29 | 75.37 | 77.56 | 79.64 | 78.41 | 79.27 | 77.97 | 74.51
9/7/2010 | ######## | 79.37 | 79.91 | 79.27 | 71.36 | 77.14 | 78.66 | 75.93 | 76.37 | 74.92 | 74 | 78.94 | 78.48 | 78.33 | 78.44 | 80.89 | 80.82 | 79.98 | 79.48 | 79.47 | 77.34 | 76.31 | 78.66 | 80.65 | 79.52 | 79.57 | 79.18 | 76.91
9/7/2010 | ######## | 79.59 | 80.79 | 80.28 | 71.36 | 77.3 | 77.99 | 76.17 | 77.51 | 76.67 | 74.37 | 80.64 | 80.02 | 79.59 | 78.55 | 80.1 | 80.24 | 81.41 | 79.48 | 80.47 | 78.5 | 78.06 | 80.16 | 82 | 80.97 | 81.14 | 80.25 | 79.05
9/7/2010 | ######## | 80.18 | 80.82 | 80.41 | 72.36 | 77.15 | 77.85 | 76.69 | 78.56 | 77.34 | 74.29 | 81.25 | 80.74 | 80.06 | 79.05 | 80.82 | 80.89 | 81.58 | 79.48 | 81.02 | 79.29 | 78.61 | 80.72 | 83.53 | 82.08 | 81.73 | 80.44 | 80.5
9/7/2010 | ######## | 80.27 | 81.57 | 80.92 | 73.55 | 77.15 | 78.76 | 77.1 | 79.33 | 78.35 | 74.4 | 81.61 | 81.9 | 80.78 | 79.38 | 81.25 | 81.72 | 81.65 | 79.92 | 81.49 | 79.57 | 79.62 | 80.76 | 84.31 | 82.79 | 82.36 | 80.54 | 81.06
9/7/2010 | ######## | 81 | 81.65 | 81.21 | 74.3 | 77.15 | 79.65 | 78.53 | 79.75 | 79.37 | 73.85 | 82.83 | 82.54 | 82.44 | 80.35 | 82.58 | 83.16 | 83.17 | 80.84 | 81.84 | 80.98 | 81.41 | 81.88 | 85.12 | 83.53 | 83.13 | 81.89 | 82.02
9/7/2010 | ######## | 81 | 82.23 | 81.78 | 74.55 | 77.15 | 81.13 | 79.12 | 80.22 | 79.86 | 74.05 | 83.7 | 83.48 | 83.91 | 81.61 | 84.34 | 84.7 | 84.35 | 82.73 | 82.38 | 82.13 | 82.23 | 82.36 | 85.66 | 84.62 | 84.58 | 83.27 | 82.84
9/7/2010 | ######## | 81.72 | 82.85 | 82.78 | 75.62 | 77.15 | 82.16 | 79.12 | 80.99 | 80.58 | 74.36 | 83.88 | 83.73 | 84.85 | 83.05 | 85.35 | 85.5 | 86.01 | 84.49 | 83.52 | 83.93 | 82.8 | 83.06 | 86.51 | 84.66 | 85.08 | 84.53 | 84.06
9/7/2010 | ######## | 81.82 | 82.43 | 82.86 | 75.86 | 76.72 | 82.69 | 78.88 | 81.06 | 81.26 | 73.87 | 83.88 | 83.73 | 85.06 | 83.59 | 86.04 | 86.79 | 87.32 | 85.2 | 83.54 | 84.61 | 82.8 | 83.22 | 86.53 | 84.72 | 85.08 | 83.91 | 84.26
9/8/2010 | ######## | 80.18 | 80.64 | 80.39 | 74.3 | 76.55 | 81.47 | 77.47 | 77.03 | 78.39 | 74.2 | 82.18 | 80.42 | 80.89 | 81.25 | 84.34 | 85.03 | 83.32 | 80.87 | 81.86 | 80.54 | 78.73 | 79.92 | 79.73 | 77.04 | 80.93 | 80.39 | 80.91
9/8/2010 | ######## | 80.18 | 79.34 | 80.34 | 74.3 | 76.58 | 80.8 | 77.47 | 77 | 77.54 | 73.81 | 81.36 | 79.74 | 80.89 | 80.74 | 83.52 | 83.52 | 82.62 | 80.05 | 81.86 | 80.41 | 78.73 | 79.9 | 79.73 | 77.6 | 80.88 | 80.39 | 80.91
9/8/2010 | ######## | 80.57 | 79.28 | 79.57 | 74.54 | 77.33 | 81.33 | 77.47 | 77.92 | 77.8 | 74.14 | 80.53 | 80.53 | 80.89 | 80.85 | 83.44 | 83.16 | 82.59 | 80.28 | 81.86 | 80.73 | 79.09 | 79.9 | 80.89 | 79.69 | 80.88 | 81.01 | 81.43
9/8/2010 | ######## | 80.99 | 80.23 | 80.13 | 75.05 | 77.3 | 81.34 | 77.47 | 78.7 | 78.4 | 74.25 | 81.75 | 81.75 | 81.46 | 81 | 83.98 | 83.59 | 83.33 | 80.28 | 82.56 | 81.24 | 80.3 | 80.77 | 81.89 | 81 | 81.67 | 81.63 | 82.51
9/8/2010 | ######## | 81.07 | 81.21 | 81.05 | 75.05 | 76.56 | 81.19 | 77.98 | 79.58 | 79.57 | 74.25 | 83.44 | 82.4 | 82.11 | 81 | 82.58 | 83.62 | 83.33 | 80.72 | 82.68 | 81.54 | 81.17 | 81.96 | 83.45 | 82.35 | 82.59 | 82.49 | 83.65
9/8/2010 | ######## | 81.8 | 82.11 | 82.01 | 75.26 | 76.56 | 82.42 | 78.28 | 80.18 | 80.15 | 74.25 | 84.09 | 83.05 | 83.23 | 81.61 | 82.58 | 83.66 | 83.36 | 81.1 | 82.68 | 81.71 | 81.77 | 82.4 | 84.75 | 83.52 | 84 | 83.66 | 84.3
9/8/2010 | ######## | 82.59 | 82.49 | 82.01 | 75.81 | 76.94 | 82.51 | 78.96 | 80.67 | 80.75 | 74.25 | 84.7 | 83.91 | 83.73 | 81.9 | 83.91 | 84.63 | 84.23 | 81.32 | 82.68 | 83.01 | 82.8 | 82.67 | 85.2 | 84.47 | 84.77 | 83.85 | 85.15
9/8/2010 | ######## | 82.64 | 82.6 | 82.77 | 76.42 | 77.36 | 83.21 | 79.07 | 81.67 | 80.75 | 74.25 | 84.85 | 84.74 | 84.78 | 83.08 | 85.03 | 85.86 | 85.21 | 82.39 | 83.25 | 84.05 | 83.3 | 83.5 | 85.76 | 85.26 | 85.76 | 84.35 | 85.71
9/8/2010 | ######## | 83.24 | 83.32 | 82.86 | 76.58 | 77.15 | 83.01 | 79.07 | 81.64 | 81.58 | 74.25 | 85.57 | 85.39 | 85.03 | 84.38 | 85.93 | 86.9 | 85.96 | 83.63 | 83.51 | 84.73 | 83.76 | 84.11 | 86.56 | 85.97 | 86.6 | 84.79 | 86.01
9/8/2010 | ######## | 83.48 | 83.22 | 82.86 | 76.58 | 76.89 | 84.51 | 79.07 | 81.04 | 81.58 | 74.04 | 85.57 | 85.6 | 85.68 | 84.45 | 85.93 | 87.84 | 87.12 | 83.8 | 83.67 | 84.73 | 83.76 | 84.11 | 86.63 | 86.16 | 86.79 | 84.79 | 86.01
9/9/2010 | ######## | 76.17 | 75.5 | 75.2 | 72.78 | 76.78 | 78.63 | 75.9 | 75.4 | 72.75 | 73.82 | 76.64 | 78.84 | 76.03 | 77 | 77.04 | 78.19 | 74.98 | 75.99 | 79.82 | 74.36 | 72.61 | 74.24 | 76.73 | 75.97 | 76.4 | 74.53 | 75.84
9/9/2010 | ######## | 75.21 | 74.94 | 74.09 | 72.78 | 76.78 | 78.7 | 75.9 | 74.83 | 71.95 | 74.14 | 76.35 | 79.27 | 75.13 | 76.21 | 76.24 | 77.43 | 74.15 | 75.29 | 78.98 | 73.96 | 71.89 | 73.5 | 75.75 | 75.47 | 75.9 | 74.03 | 74.93
9/9/2010 | ######## | 76.08 | 75.91 | 75.18 | 72.78 | 76.78 | 78.8 | 75.92 | 75.45 | 73.71 | 74.29 | 78.19 | 80.02 | 75.78 | 76.57 | 76.89 | 78.22 | 74.76 | 75.36 | 78.56 | 74.12 | 73.96 | 75.3 | 77.23 | 77.02 | 77.04 | 76.34 | 76.82
9/9/2010 | ######## | 77.64 | 77.72 | 77.01 | 72.72 | 76.78 | 77.19 | 76.67 | 76.14 | 75.54 | 73.79 | 80.13 | 80.46 | 77.18 | 77.68 | 78.44 | 80.06 | 76.35 | 76.15 | 78.56 | 74.94 | 75.77 | 77.32 | 79.33 | 79.03 | 79.18 | 78.5 | 79.15
9/9/2010 | ######## | 78.34 | 78.25 | 77.85 | 72.73 | 76.78 | 75.65 | 76.67 | 76.14 | 76.2 | 73.79 | 81 | 80.46 | 78.26 | 78.3 | 79.27 | 80.71 | 77.25 | 76.83 | 78.56 | 75.45 | 76.73 | 78.08 | 80.51 | 80.06 | 80.11 | 79.4 | 80.45
9/9/2010 | ######## | 78.34 | 78.83 | 78.53 | 72.73 | 76.78 | 75.56 | 76.67 | 76.14 | 76.56 | 73.79 | 81 | 81.25 | 79.02 | 78.44 | 79.81 | 81.46 | 77.98 | 77.41 | 78.56 | 75.45 | 76.83 | 78.69 | 81.28 | 80.84 | 80.68 | 80.07 | 81.26
9/9/2010 | ######## | 78.81 | 78.83 | 78.53 | 72.73 | 76.78 | 76.22 | 76.67 | 76.14 | 76.56 | 73.88 | 81 | 81.25 | 79.02 | 79.02 | 80.31 | 81.64 | 78.53 | 77.65 | 78.56 | 76.11 | 76.83 | 78.69 | 81.28 | 80.86 | 80.68 | 80.2 | 81.26
9/9/2010 | ######## | 79.13 | 78.83 | 78.53 | 72.73 | 76.78 | 77.26 | 76.67 | 76.14 | 76.56 | 73.79 | 81.28 | 81.25 | 79.66 | 79.41 | 80.67 | 82.33 | 79.39 | 78.56 | 78.92 | 76.41 | 77.01 | 78.69 | 81.28 | 80.86 | 80.68 | 80.2 | 81.73
9/9/2010 | ######## | 79.13 | 78.83 | 78.53 | 72.73 | 76.78 | 77.9 | 76.67 | 76.14 | 76.56 | 73.79 | 81.82 | 81.25 | 80.6 | 80.06 | 81.75 | 83.12 | 81.01 | 79.79 | 79.36 | 77.6 | 77.61 | 79.05 | 81.28 | 80.86 | 81.19 | 80.2 | 82.07
9/9/2010 | ######## | 79.13 | 78.83 | 78.53 | 72.73 | 76.78 | 79.02 | 76.67 | 76.14 | 76.56 | 73.79 | 81.82 | 81.25 | 80.64 | 80.06 | 81.93 | 83.95 | 81.26 | 80.01 | 79.36 | 77.77 | 77.61 | 79.49 | 82.09 | 80.86 | 81.5 | 80.2 | 82.07
9/10/2010 | ######## | 75.16 | 74.54 | 73.65 | 70.32 | 75.87 | 76.15 | 73.82 | 73.77 | 71.95 | 74.02 | 75.2 | 76.46 | 73.58 | 74.55 | 75.27 | 75.96 | 71.93 | 72.78 | 76.25 | 70.29 | 70.3 | 73 | 75.28 | 74.14 | 74.62 | 73.09 | 74.72
9/10/2010 | ######## | 74.53 | 74.15 | 72.92 | 68.26 | 75.87 | 75.09 | 72.87 | 73.86 | 72.22 | 74.09 | 74.91 | 76.71 | 73.36 | 74.44 | 74.8 | 75.7 | 71.56 | 72.53 | 75.42 | 70.11 | 70.41 | 72.93 | 74.91 | 74.18 | 74.54 | 73.63 | 74.43
9/10/2010 | ######## | 75.98 | 76.67 | 74.35 | 68.75 | 75.87 | 74.78 | 73.52 | 75.43 | 73.18 | 74.29 | 76.24 | 77.76 | 74.73 | 75.09 | 76.21 | 77.47 | 72.72 | 73.85 | 75.42 | 71.11 | 73.12 | 75.67 | 76.81 | 76.84 | 76.45 | 76.89 | 76.77
9/10/2010 | ######## | 78.23 | 77.85 | 76.74 | 69.58 | 76.23 | 75.45 | 74.44 | 77.03 | 73.5 | 74.29 | 78.3 | 78.04 | 76.24 | 75.56 | 77.18 | 78.87 | 74.84 | 75.44 | 76.43 | 72.85 | 74.71 | 77.53 | 78.65 | 79.8 | 78.79 | 79.13 | 79.38
9/10/2010 | ######## | 79.08 | 77.01 | 77.94 | 69.32 | 76.64 | 73.79 | 75.11 | 77.71 | 74.25 | 74.29 | 78.48 | 78.04 | 77.58 | 75.52 | 77.65 | 79.52 | 76.1 | 76.45 | 77.46 | 72.94 | 74.9 | 78.39 | 79.89 | 80.76 | 79.37 | 79.43 | 80.89
9/10/2010 | ######## | 79.83 | 78.03 | 78.26 | 70.04 | 76.64 | 72.29 | 75.11 | 77.71 | 74.85 | 74.29 | 79.09 | 78.04 | 78.62 | 75.88 | 77.18 | 79.52 | 77.05 | 77.18 | 77.73 | 73.84 | 75.04 | 79.33 | 81.08 | 80.76 | 80.49 | 80.06 | 81.97
9/10/2010 | ######## | 79.89 | 77.43 | 77.54 | 70.34 | 77.04 | 73.64 | 75.75 | 77.71 | 75.4 | 73.59 | 79.95 | 78.44 | 79.56 | 76.53 | 78.66 | 80.38 | 78.3 | 78.15 | 77.73 | 75 | 76.6 | 79.49 | 81.3 | 80.76 | 81.07 | 80.78 | 81.97
9/10/2010 | ######## | 80.69 | 76.94 | 76.7 | 70.34 | 76.49 | 74.59 | 75.87 | 77.71 | 75.08 | 73.66 | 79.92 | 78.51 | 79.63 | 76.46 | 79.3 | 81.25 | 79.24 | 78.84 | 78.8 | 75.35 | 76.98 | 80.16 | 81.88 | 80.76 | 81.88 | 81.05 | 81.97
9/10/2010 | ######## | 80.7 | 77.61 | 77.05 | 70.34 | 76.49 | 75.15 | 75.87 | 77.71 | 74.92 | 73.55 | 79.23 | 77.58 | 79.63 | 76.53 | 78.84 | 81.75 | 80.09 | 79.96 | 79.93 | 77.49 | 77.39 | 80.29 | 81.85 | 80.76 | 82.11 | 81.45 | 81.95
9/10/2010 | ######## | 80.7 | 77.72 | 75.86 | 70.34 | 76.49 | 76.06 | 75.87 | 77 | 73.75 | 73.95 | 79.23 | 78.15 | 79.63 | 77.25 | 79.52 | 81.07 | 80.26 | 79.99 | 80.11 | 77.12 | 76.47 | 79.62 | 81.3 | 80.76 | 80.71 | 79.51 | 80.95

## Slide 15: 2010: 9/13-9/17
9/13/2010 | ######## | 72.63 | 71.76 | 70.86 | 66.13 | 73.47 | 73.25 | 69.62 | 70.16 | 68.88 | 73.72 | 71.24 | 71.28 | 70.66 | 70.48 | 72.07 | 73.36 | 72.2 | 70.55 | 72.22 | 69.32 | 66.22 | 67.64 | 70.12 | 69.8 | 70.24 | 69.61 | 70.46
9/13/2010 | ######## | 71.97 | 71.54 | 70.39 | 66.13 | 73.47 | 72.51 | 69.22 | 69.99 | 68.82 | 74.22 | 70.63 | 71.67 | 70.45 | 70.09 | 71.96 | 72.93 | 71.59 | 70.33 | 71.62 | 69.32 | 66.48 | 67.87 | 69.77 | 69.54 | 69.73 | 69.56 | 69.93
9/13/2010 | ######## | 72.23 | 72.68 | 71.58 | 66.24 | 73.71 | 72.41 | 69.88 | 71.11 | 69.84 | 74.07 | 70.84 | 73.22 | 70.92 | 70.84 | 73.04 | 73.8 | 72.11 | 71.67 | 71.99 | 70.2 | 67.85 | 69.76 | 71.19 | 70.95 | 70.65 | 72.11 | 71.3
9/13/2010 | ######## | 72.7 | 72.91 | 72 | 67.17 | 74.44 | 73.66 | 69.96 | 72.36 | 70.54 | 74.16 | 72.64 | 73.87 | 71.71 | 71.82 | 73.65 | 75.38 | 72.75 | 72.67 | 72.73 | 70.79 | 69.31 | 70.48 | 72.65 | 71.71 | 71.15 | 72.52 | 72.21
9/13/2010 | ######## | 73.97 | 74.61 | 73.83 | 68.35 | 75.05 | 73.54 | 70.62 | 73.37 | 71.67 | 74.34 | 72.93 | 74.88 | 72.82 | 73.33 | 74.55 | 75.56 | 73.41 | 73.07 | 73.58 | 70.79 | 70.83 | 71.68 | 74.55 | 73.21 | 71.93 | 72.53 | 73.62
9/13/2010 | ######## | 74.43 | 75.21 | 74.77 | 68.87 | 76.01 | 73.54 | 70.62 | 73.86 | 71.75 | 73.94 | 73.8 | 75.06 | 73.15 | 73.11 | 73.87 | 75.02 | 74.48 | 73.63 | 73.81 | 71.07 | 71.01 | 72.25 | 75.1 | 73.59 | 73.39 | 73.46 | 73.6
9/13/2010 | ######## | 74.99 | 74.57 | 74.12 | 68.21 | 76.5 | 74.05 | 71.28 | 73.86 | 72.1 | 74.33 | 74.44 | 75.52 | 73.04 | 72.1 | 74.62 | 75.42 | 75.11 | 73.9 | 73.81 | 72.02 | 71.99 | 72.52 | 75.2 | 73.87 | 74.41 | 74.35 | 73.72
9/13/2010 | ######## | 74.99 | 75.75 | 74.21 | 68.69 | 76.5 | 74.78 | 71.34 | 74.3 | 72.5 | 74.14 | 75.34 | 76.24 | 73.76 | 72.54 | 74.7 | 76.68 | 75.85 | 74.77 | 74.49 | 72.65 | 72.59 | 73.41 | 75.61 | 74.57 | 75.4 | 74.97 | 74.51
9/13/2010 | ######## | 75.62 | 75.81 | 74.94 | 68.92 | 76.5 | 75.22 | 71.34 | 73.86 | 73.06 | 74.26 | 75.88 | 76.57 | 74.55 | 74.26 | 74.84 | 77.36 | 77.46 | 75.89 | 75.32 | 72.99 | 72.92 | 74.15 | 76.25 | 75.09 | 76.15 | 75.58 | 74.68
9/13/2010 | ######## | 75.6 | 74.97 | 73.71 | 68.92 | 76.5 | 75.53 | 71.34 | 73.23 | 72.49 | 73.99 | 74.59 | 76.14 | 74.12 | 74.23 | 75.2 | 77.36 | 76.83 | 75.43 | 75.32 | 72.99 | 72.15 | 73.43 | 75.92 | 75.09 | 75.68 | 75.08 | 74.18
9/14/2010 | ######## | 72.81 | 71.18 | 71.3 | 66.83 | 73.77 | 73.59 | 69.64 | 70.43 | 69.09 | 73.73 | 71.24 | 71.96 | 71.17 | 70.88 | 72.07 | 72.5 | 72.17 | 70.73 | 73.04 | 70.06 | 66.93 | 68.93 | 71.24 | 70.73 | 70.99 | 69.87 | 71.13
9/14/2010 | ######## | 72.09 | 70.97 | 70.84 | 66.83 | 73.47 | 72.88 | 69.17 | 70.44 | 69.24 | 73.9 | 70.95 | 72.21 | 71.17 | 70.81 | 71.6 | 72.5 | 71.57 | 70.32 | 72.66 | 70.14 | 66.94 | 68.98 | 70.71 | 70.74 | 70.66 | 69.92 | 70.42
9/14/2010 | ######## | 73.62 | 73.86 | 73.22 | 67.74 | 73.89 | 73.23 | 69.59 | 72.49 | 71.13 | 74.07 | 72.93 | 74.23 | 71.92 | 71.89 | 73.18 | 73.51 | 72.82 | 72.13 | 73 | 70.82 | 69.51 | 71.91 | 73.2 | 72.94 | 72.49 | 72.3 | 72.21
9/14/2010 | ######## | 74.46 | 74.72 | 74.07 | 68.7 | 75.14 | 73.77 | 70.54 | 73.73 | 72.22 | 73.9 | 74.26 | 75.27 | 73.04 | 72.57 | 74.05 | 74.77 | 73.37 | 73.04 | 73.29 | 71.48 | 71.8 | 72.83 | 75.26 | 74.37 | 73.53 | 73.67 | 73.98
9/14/2010 | ######## | 75.5 | 75.38 | 74.82 | 69.31 | 75.87 | 74.35 | 71.24 | 74.59 | 73.35 | 73.9 | 74.98 | 76.93 | 74.08 | 73.29 | 75.2 | 75.49 | 74.11 | 73.53 | 74.21 | 71.7 | 73.16 | 73.46 | 76.25 | 75.29 | 74.4 | 74.77 | 75.52
9/14/2010 | ######## | 76.57 | 76.41 | 76.26 | 69.95 | 76.35 | 74.57 | 71.7 | 75.23 | 74.15 | 73.8 | 76.89 | 77.5 | 75.92 | 74.48 | 75.42 | 76.14 | 75.66 | 74.38 | 74.52 | 73.69 | 74.52 | 74.31 | 77.33 | 77.22 | 76.68 | 76.33 | 77.02
9/14/2010 | ######## | 77.18 | 76.89 | 77.13 | 70.28 | 76.65 | 75.19 | 72.23 | 75.41 | 75.15 | 73.85 | 78.66 | 78.22 | 77.79 | 75.2 | 76.68 | 77.9 | 76.91 | 75.93 | 74.62 | 75.46 | 75.91 | 75.51 | 78.4 | 78.71 | 78.52 | 77.31 | 78.13
9/14/2010 | ######## | 77.75 | 77.71 | 77.17 | 70.37 | 76.65 | 75.19 | 72.77 | 75.5 | 75.26 | 73.79 | 78.94 | 77.79 | 78.76 | 75.45 | 77.29 | 78.91 | 77.65 | 76.45 | 75.79 | 75.87 | 76.76 | 76.32 | 78.96 | 79.08 | 79.68 | 78.55 | 78.98
9/14/2010 | ######## | 77.97 | 78.31 | 77.92 | 70.76 | 76.65 | 75.15 | 72.77 | 76.18 | 75.26 | 73.92 | 77.54 | 76.17 | 78.76 | 76.28 | 77.65 | 79.56 | 78.69 | 77.39 | 76.83 | 77.26 | 76.94 | 76.6 | 79.64 | 78.45 | 79.95 | 79.03 | 79.45
9/14/2010 | ######## | 77.97 | 78.31 | 77.92 | 70.97 | 76.65 | 74.81 | 72.77 | 76.18 | 75.12 | 73.82 | 77.5 | 76.57 | 79.3 | 77.36 | 78.55 | 81.79 | 81.04 | 78.26 | 76.83 | 78.66 | 76.77 | 76.6 | 79.76 | 78.29 | 79.95 | 78.12 | 78.73
9/14/2010 | ######## | 77.97 | 77.9 | 77.19 | 70.97 | 76.65 | 75.62 | 72.77 | 75.76 | 74.5 | 73.86 | 77.5 | 76.57 | 79.56 | 78.22 | 79.59 | 84.27 | 82.93 | 80.42 | 76.83 | 78.76 | 76.16 | 76.6 | 79.76 | 77.97 | 79.01 | 77.44 | 78.56
9/15/2010 | ######## | 71.3 | 70.09 | 69.18 | 65.93 | 73.65 | 72.18 | 67.82 | 70.07 | 66.93 | 73.72 | 69.51 | 71.6 | 71.78 | 70.34 | 72 | 71.78 | 72.07 | 70.86 | 72.65 | 69.93 | 65.88 | 67.53 | 69.82 | 69.3 | 70.09 | 67.71 | 67.96
9/15/2010 | ######## | 70.5 | 69.54 | 68.27 | 63.48 | 73.65 | 72.18 | 67.51 | 70.13 | 67.32 | 73.99 | 69.44 | 71.6 | 71.2 | 69.8 | 71.17 | 71.42 | 71.02 | 70.24 | 72.07 | 69.9 | 66.26 | 67.43 | 69.46 | 69.25 | 69.93 | 68.23 | 67.59
9/15/2010 | ######## | 72.87 | 73.2 | 71.63 | 66.39 | 73.67 | 72.18 | 68.98 | 71.58 | 70.45 | 74.12 | 71.42 | 74.41 | 72.57 | 71.31 | 72.43 | 72.97 | 71.12 | 71.64 | 72.54 | 69.9 | 69.13 | 70.81 | 72.44 | 72.41 | 72.02 | 72.29 | 70.82
9/15/2010 | ######## | 74.27 | 75 | 73.91 | 68.48 | 74.39 | 72.18 | 70.38 | 73.43 | 71.79 | 74.12 | 74.19 | 75.38 | 74.05 | 72.54 | 72.9 | 73.58 | 72.81 | 72.22 | 73.42 | 69.9 | 71.48 | 72.69 | 74.4 | 74.83 | 74.27 | 73.38 | 73.05
9/15/2010 | ######## | 75.17 | 75.92 | 74.71 | 68.34 | 75.3 | 70.85 | 71.67 | 74.29 | 72.7 | 74.2 | 75.74 | 74.8 | 74.91 | 74.12 | 73.98 | 75.31 | 73.56 | 73.44 | 74.09 | 69.7 | 72.57 | 73.87 | 76.19 | 76.23 | 75.48 | 74.96 | 74.88
9/15/2010 | ######## | 76.01 | 76.83 | 75.36 | 67.15 | 76.23 | 72.19 | 71.67 | 74.53 | 73.85 | 74.87 | 75.34 | 73.94 | 76.46 | 75.49 | 75.27 | 76.28 | 73.92 | 74.67 | 74.71 | 70.72 | 73.46 | 74.66 | 77.47 | 77.59 | 76.47 | 74.73 | 75.85
9/15/2010 | ######## | 76.23 | 76.83 | 75.36 | 67.15 | 76.71 | 73.03 | 72.33 | 74.85 | 74.69 | 74.48 | 76.32 | 74.16 | 77.54 | 75.67 | 75.96 | 76.75 | 75.1 | 76.08 | 75.04 | 72.49 | 73.92 | 75.49 | 78.38 | 78.25 | 77.97 | 75.48 | 76.49
9/15/2010 | ######## | 76.89 | 76.83 | 76.02 | 67.15 | 76.9 | 73.54 | 72.39 | 75.31 | 75.22 | 74.08 | 77.9 | 74.55 | 78.19 | 76.03 | 76.1 | 77.83 | 76.41 | 77.02 | 75.39 | 72.91 | 74.63 | 76.61 | 79.25 | 79.09 | 79.29 | 76.66 | 76.91
9/15/2010 | ######## | 77.71 | 77.44 | 76.11 | 67.15 | 76.96 | 73.8 | 72.39 | 74.65 | 75.22 | 74.25 | 78.3 | 75.2 | 78.76 | 77.22 | 75.85 | 78.73 | 78.29 | 78.31 | 76.33 | 73.46 | 75.05 | 76.99 | 79.63 | 79.46 | 80.24 | 76.12 | 76.91
9/15/2010 | ######## | 77.79 | 77.7 | 76.11 | 67.31 | 76.67 | 74.86 | 72.39 | 74.55 | 75.22 | 75.65 | 78.3 | 75.31 | 79.3 | 77.65 | 76.82 | 80.64 | 78.89 | 79.94 | 76.58 | 74.19 | 75.05 | 76.85 | 79.63 | 79.46 | 79.75 | 74 | 76.91
9/16/2010 | ######## | 69.75 | 69.14 | 67.14 | 65.13 | 72.94 | 69.8 | 66.46 | 68.86 | 65.82 | 73.47 | 68.29 | 70.02 | 70.63 | 68.94 | 69.22 | 70.77 | 69.72 | 69.02 | 71.28 | 68.39 | 66.1 | 66.02 | 68.15 | 67.6 | 69.27 | 65.83 | 66.25
9/16/2010 | ######## | 68.65 | 69.05 | 66.28 | 65.13 | 72.84 | 69.17 | 65.91 | 68.76 | 66.47 | 73.95 | 67.6 | 69.98 | 70.27 | 68.29 | 68.72 | 70.23 | 68.59 | 68.31 | 70.51 | 68.35 | 65.88 | 66.38 | 67.78 | 67.39 | 68.89 | 66.6 | 66.6
9/16/2010 | ######## | 69.78 | 69.94 | 68.07 | 66 | 72.84 | 69.19 | 67.33 | 70.23 | 68.67 | 74.48 | 69.51 | 72.64 | 71.13 | 69.8 | 69.87 | 71.31 | 68.68 | 68.6 | 71.03 | 69.39 | 68.24 | 69.66 | 70.7 | 71.23 | 70.36 | 69.99 | 68.23
9/16/2010 | ######## | 71.67 | 72.58 | 71.14 | 67.54 | 73.54 | 68.19 | 68.87 | 72.27 | 70.29 | 74.05 | 72.93 | 74.26 | 72.68 | 71.42 | 70.88 | 72.07 | 71.38 | 70.1 | 72.32 | 70.14 | 70.16 | 71.73 | 72.87 | 73.2 | 72.57 | 71.66 | 71.27
9/16/2010 | ######## | 73.03 | 74.08 | 72.81 | 67.86 | 74.76 | 68.8 | 70.75 | 73.47 | 71.41 | 73.92 | 75.13 | 74.91 | 74.05 | 73.04 | 71.67 | 73.26 | 72.48 | 71.67 | 73.27 | 70.1 | 71.57 | 73.01 | 74.75 | 74.53 | 73.55 | 72.67 | 72.27
9/16/2010 | ######## | 74.7 | 75.57 | 74.56 | 68.37 | 75.87 | 69.74 | 70.75 | 74.08 | 72.7 | 74.64 | 75.02 | 74.98 | 75.81 | 74.3 | 73.51 | 74.95 | 73.5 | 73.24 | 74.28 | 69.85 | 72.88 | 73.7 | 76.32 | 75.36 | 74.75 | 73.72 | 73.68
9/16/2010 | ######## | 75.89 | 76.32 | 75.34 | 68.55 | 76.65 | 71.06 | 71.46 | 74.3 | 74.04 | 74.64 | 76.03 | 75.24 | 77.4 | 75.56 | 74.34 | 75.7 | 74.52 | 75.14 | 75.05 | 71.67 | 74.32 | 74.76 | 77.55 | 75.87 | 76.74 | 74.84 | 75.33
9/16/2010 | ######## | 76.53 | 76.35 | 74.72 | 68.55 | 76.65 | 71.78 | 71.87 | 75.02 | 74.5 | 74.64 | 76.86 | 75.42 | 78.33 | 76.39 | 76.32 | 77.54 | 76.24 | 76.17 | 76.21 | 73.52 | 75.19 | 76.18 | 78.36 | 76.12 | 78.23 | 75.9 | 76.69
9/16/2010 | ######## | 76.53 | 77.1 | 75.36 | 68.55 | 76.65 | 72.28 | 72.19 | 75.23 | 75.08 | 74.52 | 76.21 | 74.59 | 78.62 | 77.36 | 77.86 | 77.94 | 78.12 | 77.15 | 76.58 | 75.46 | 75.54 | 76.25 | 78.73 | 75.77 | 79.25 | 75.76 | 77.47
9/16/2010 | ######## | 76.53 | 77.1 | 75.36 | 68.55 | 76.65 | 71.73 | 72.19 | 74.59 | 74.57 | 76.23 | 76.21 | 75.34 | 78.62 | 77.76 | 76.03 | 78.58 | 80.01 | 77.48 | 77.31 | 76.7 | 75.54 | 76.25 | 78.73 | 75.99 | 79.25 | 73.63 | 77.47
9/17/2010 | ######## | 74.22 | 73.52 | 73.55 | 67.86 | 74.3 | 75.58 | 71.47 | 72.95 | 72.27 | 73.63 | 73.94 | 73.87 | 74.19 | 74.26 | 75.06 | 74.73 | 75.7 | 73.48 | 75.64 | 71.78 | 71.41 | 72.54 | 74.96 | 74.06 | 74.58 | 73.35 | 73.63
9/17/2010 | ######## | 74.22 | 73.44 | 73.1 | 67.86 | 74.35 | 75.47 | 71.47 | 72.95 | 72.42 | 74.33 | 73.94 | 74.23 | 73.98 | 74.26 | 75.09 | 74.91 | 75.7 | 73.63 | 75.03 | 71.89 | 71.37 | 72.62 | 74.94 | 73.92 | 74.58 | 73.54 | 73.63
9/17/2010 | ######## | 74.67 | 74.76 | 74.06 | 68.16 | 75.51 | 76 | 71.47 | 74.63 | 75.08 | 74.33 | 74.01 | 76.06 | 74.44 | 74.84 | 76.75 | 76.53 | 75.7 | 76.05 | 75.03 | 73.12 | 72.16 | 74.18 | 77.14 | 74.93 | 74.65 | 75.14 | 73.86
9/17/2010 | ######## | 74.96 | 74.85 | 74.61 | 69.37 | 76.37 | 76.25 | 71.81 | 75.82 | 75.45 | 74.33 | 75.67 | 76.96 | 75.2 | 75.67 | 77.29 | 77.36 | 76.76 | 78.01 | 75.71 | 73.95 | 73.66 | 75.38 | 79.01 | 75.87 | 75.93 | 76.14 | 75.62
9/17/2010 | ######## | 75.35 | 75.93 | 75.74 | 70.4 | 76.82 | 76.25 | 73.19 | 75.86 | 75.31 | 74.33 | 76.82 | 76.96 | 75.52 | 75.81 | 77.07 | 77.25 | 77.49 | 77.9 | 76.57 | 74.78 | 74.68 | 75.5 | 78.6 | 76.65 | 76.13 | 76.41 | 75.96
9/17/2010 | ######## | 75.72 | 75.24 | 75.27 | 70.67 | 77.4 | 76.25 | 72.35 | 75.27 | 75.35 | 74.16 | 75.56 | 76.14 | 75.52 | 75.52 | 77.18 | 77.22 | 75.76 | 77.29 | 76.57 | 74.1 | 73.65 | 74.46 | 78.25 | 76.61 | 75.76 | 75.91 | 74.69
9/17/2010 | ######## | 75.72 | 74.56 | 73.92 | 70.67 | 76.76 | 76.25 | 72.2 | 75.76 | 75.13 | 73.86 | 75.34 | 75.31 | 75.52 | 74.7 | 77.18 | 77.43 | 76.12 | 77.93 | 75.84 | 72.25 | 72.69 | 74.57 | 78.58 | 76.12 | 76.07 | 75.65 | 74.9
9/17/2010 | ######## | 75.72 | 75.48 | 74.39 | 70.67 | 77.15 | 76.25 | 72.2 | 74.21 | 72.03 | 73.67 | 76.53 | 76.21 | 75.52 | 74.37 | 76.28 | 77.14 | 77.11 | 77.58 | 75.79 | 71.88 | 71.99 | 75.44 | 76.7 | 76.12 | 76.86 | 76.31 | 74.96
9/17/2010 | ######## | 75.28 | 75.11 | 73.83 | 70.67 | 77.02 | 75.89 | 71.51 | 73.28 | 70.37 | 73.98 | 78.01 | 77.54 | 75.52 | 73.72 | 75.67 | 76.35 | 76.48 | 77.34 | 75.79 | 71.67 | 70.82 | 75.04 | 76.71 | 74.78 | 76.12 | 74.15 | 74.14
9/17/2010 | ######## | 74.94 | 75.5 | 73.83 | 70.67 | 76.59 | 76.11 | 71.46 | 72.89 | 67.99 | 76.26 | 76.93 | 76.89 | 75.52 | 71.74 | 76.17 | 74.77 | 76.23 | 76.79 | 75.79 | 72.73 | 68.78 | 75.35 | 77.18 | 72.35 | 76.12 | 71.51 | 74.79

## Slide 16: 2010: 9/20-9/24
9/20/2010 | ######## | 71.63 | 70.43 | 70.3 | 66.47 | 72.79 | 72.03 | 68.34 | 69.55 | 68.2 | 73.66 | 70.81 | 71.53 | 71.89 | 70.16 | 70.81 | 71.6 | 69.65 | 69.15 | 71.42 | 69.36 | 67.03 | 68.25 | 70.63 | 69.87 | 70.34 | 70.08 | 70.67
9/20/2010 | ######## | 71.18 | 69.91 | 69.62 | 66.47 | 72.75 | 71.34 | 67.87 | 69.42 | 68.41 | 74 | 70.3 | 71.71 | 71.74 | 69.55 | 70.12 | 71.02 | 69.03 | 68.84 | 70.85 | 69.28 | 66.89 | 68.38 | 69.87 | 69.64 | 69.67 | 70.04 | 70.02
9/20/2010 | ######## | 72.45 | 72.58 | 71.91 | 67.18 | 72.75 | 71.22 | 65.3 | 70.88 | 70.12 | 74 | 71.02 | 73.69 | 72.68 | 70.7 | 71.24 | 72.21 | 69.77 | 70.03 | 71.15 | 70.34 | 69.36 | 70.86 | 72.37 | 72.11 | 71.54 | 72.79 | 72.52
9/20/2010 | ######## | 73.77 | 74.12 | 73.72 | 67.82 | 74.06 | 70.37 | 68.26 | 72.59 | 71.3 | 74 | 73.72 | 74.52 | 74.08 | 72.43 | 72.14 | 73 | 71.1 | 71.33 | 72.35 | 70.76 | 71.89 | 72.77 | 74.48 | 74.15 | 73.87 | 74.61 | 73.78
9/20/2010 | ######## | 74.92 | 74.88 | 75.2 | 67.82 | 74.61 | 68.15 | 70.53 | 73.46 | 72.25 | 74 | 75.16 | 74.01 | 75.99 | 73.62 | 73.69 | 73.11 | 72.42 | 72.15 | 73.26 | 71.86 | 73.63 | 74.06 | 76.53 | 76.41 | 75.78 | 76.18 | 76.06
9/20/2010 | ######## | 76.1 | 75.66 | 75.95 | 67.82 | 75.06 | 69 | 70.72 | 73.66 | 72.42 | 74 | 75.2 | 73.69 | 77.76 | 74.55 | 74.05 | 73.26 | 73.23 | 72.73 | 73.47 | 72.15 | 74.31 | 74.98 | 77.84 | 76.91 | 77.42 | 76.67 | 76.38
9/20/2010 | ######## | 76.41 | 75.72 | 75.95 | 67.82 | 75.06 | 70.03 | 70.72 | 73.66 | 72.97 | 74 | 75.67 | 74.01 | 79.09 | 74.84 | 74.91 | 74.98 | 74.21 | 73.86 | 73.47 | 73.15 | 75.23 | 75.56 | 77.96 | 76.56 | 77.79 | 76.99 | 77.16
9/20/2010 | ######## | 76.98 | 76.43 | 75.95 | 67.82 | 76.02 | 71.88 | 71.38 | 73.96 | 72.97 | 74 | 75.78 | 74.19 | 80.13 | 75.81 | 76.1 | 76.68 | 74.9 | 74.65 | 74.38 | 74.64 | 75.33 | 76.03 | 78.42 | 76.56 | 78.84 | 77.99 | 77.35
9/20/2010 | ######## | 77.19 | 77.15 | 75.95 | 67.82 | 76.52 | 72.92 | 71.46 | 74.71 | 73.52 | 74.18 | 74.95 | 72.93 | 80.31 | 76.86 | 77 | 78.33 | 76.86 | 76.46 | 74.99 | 76.36 | 75.33 | 76.03 | 78.85 | 75.79 | 79.2 | 77.2 | 78.57
9/20/2010 | ######## | 77.19 | 77.75 | 75.95 | 67.82 | 76.18 | 73.89 | 71.46 | 74.26 | 72.92 | 75.82 | 75.38 | 73.15 | 80.31 | 77.58 | 77.58 | 80.17 | 77.18 | 78.69 | 75.41 | 77.2 | 75.26 | 76.03 | 78.85 | 76.26 | 79.2 | 75.22 | 78.06
9/21/2010 | ######## | 67.13 | 68.92 | 66.52 | 65.13 | 73.23 | 67.71 | 66.46 | 67.38 | 66.43 | 73.53 | 66.56 | 68.25 | 68.18 | 67.28 | 65.91 | 67.42 | 66.2 | 66.35 | 69.81 | 65.48 | 64.32 | 66.17 | 66.15 | 66.24 | 66.59 | 66.12 | 66.13
9/21/2010 | ######## | 66.75 | 69.08 | 66.38 | 65.13 | 72.91 | 67.7 | 66.46 | 67.32 | 66.43 | 73.81 | 65.98 | 68.25 | 68.4 | 66.85 | 66.2 | 67.46 | 65.97 | 66.6 | 69.81 | 66.07 | 64.79 | 66.36 | 66.6 | 66.69 | 66.59 | 66.59 | 66.1
9/21/2010 | ######## | 68.9 | 70.4 | 68.83 | 65.87 | 72.74 | 67.97 | 66.7 | 69.05 | 67.24 | 74.32 | 67.21 | 71.17 | 69.98 | 68.72 | 67.82 | 68.76 | 66.3 | 68.4 | 70.48 | 68.07 | 67.52 | 68.1 | 69.72 | 69.34 | 68.78 | 69.29 | 68.57
9/21/2010 | ######## | 70.95 | 72.2 | 71.6 | 67.51 | 73.68 | 69.44 | 67.53 | 71.29 | 69.12 | 74.33 | 70.81 | 73.15 | 71.96 | 70.23 | 68.83 | 69.98 | 68.42 | 69.43 | 71.16 | 69.35 | 69.54 | 70.54 | 72.04 | 71.26 | 71.3 | 71.61 | 71.57
9/21/2010 | ######## | 72 | 73.18 | 72.78 | 68.27 | 74.28 | 69.92 | 68.51 | 72.81 | 70.41 | 73.89 | 71.56 | 74.55 | 74.01 | 71.96 | 69.98 | 71.35 | 69.34 | 70.46 | 71.68 | 69.59 | 71.14 | 71.31 | 73.84 | 72.56 | 72.42 | 72.32 | 73.21
9/21/2010 | ######## | 73.44 | 74.47 | 73.49 | 68.93 | 74.66 | 69.05 | 68.86 | 72.9 | 71.14 | 74.51 | 73.04 | 74.01 | 75.96 | 73.22 | 70.09 | 72.03 | 70.89 | 71.96 | 72 | 70.44 | 72.19 | 72.41 | 74.93 | 73.84 | 74.61 | 74.05 | 74.49
9/21/2010 | ######## | 74.71 | 75.5 | 73.49 | 69.2 | 74.81 | 69.67 | 69.62 | 73.2 | 72.13 | 74.51 | 74.23 | 74.12 | 77.43 | 73.94 | 71.64 | 73.72 | 72.15 | 73.32 | 72.09 | 72.06 | 73.47 | 73.64 | 75.62 | 74.35 | 75.81 | 74.8 | 75.43
9/21/2010 | ######## | 74.82 | 75.51 | 74.02 | 69.2 | 75.68 | 70.75 | 69.92 | 73.64 | 72.19 | 74.75 | 74.95 | 74.88 | 77.97 | 74.88 | 73.33 | 75.31 | 74.28 | 74.84 | 73.34 | 72.62 | 74.11 | 74.67 | 76.89 | 75.19 | 76.99 | 75.61 | 76.21
9/21/2010 | ######## | 75.47 | 75.51 | 74.12 | 69.2 | 76.76 | 72.07 | 69.92 | 73.64 | 72.79 | 74.67 | 76.17 | 75.09 | 78.58 | 76.42 | 74.48 | 76.39 | 76.45 | 76.77 | 74.33 | 73.93 | 74.49 | 75.5 | 77.22 | 75.11 | 77.84 | 75.64 | 76.21
9/21/2010 | ######## | 75.47 | 75.51 | 73.74 | 69.2 | 76.81 | 73.07 | 69.92 | 73.64 | 72.92 | 76.21 | 75.7 | 75.09 | 78.58 | 76.86 | 75.85 | 78.4 | 78.46 | 78.39 | 75.01 | 75.48 | 74.49 | 75.39 | 76.88 | 74.08 | 77.41 | 74.04 | 76.21
9/22/2010 | ######## | 72.48 | 71.51 | 71.93 | 67.81 | 74.51 | 74.1 | 69.21 | 70.68 | 70 | 73.74 | 71.67 | 72.75 | 73.15 | 73 | 73.22 | 73.87 | 72.93 | 73 | 74.27 | 70.46 | 68.8 | 70.43 | 72.59 | 71.1 | 71.96 | 71.7 | 72.58
9/22/2010 | ######## | 72.48 | 71.14 | 71.93 | 67.81 | 74.51 | 74.05 | 69.21 | 70.73 | 70.32 | 74.1 | 71.89 | 72.97 | 73.15 | 73 | 73.04 | 73 | 72.5 | 72.97 | 74.27 | 70.63 | 68.99 | 70.78 | 72.64 | 71.28 | 72.1 | 72.1 | 72.54
9/22/2010 | ######## | 73.28 | 73.25 | 72.98 | 68.56 | 74.84 | 74.05 | 70.06 | 72.22 | 72.27 | 74.34 | 73.15 | 75.13 | 74.23 | 74.19 | 74.3 | 73.29 | 72.8 | 74.33 | 74.27 | 72.11 | 71.86 | 73.29 | 74.92 | 73.4 | 74.1 | 74.17 | 74.69
9/22/2010 | ######## | 74.79 | 75.42 | 76.02 | 70.35 | 75.85 | 73.86 | 72.37 | 74.16 | 73.65 | 73.92 | 76.46 | 76.42 | 75.63 | 75.45 | 75.49 | 74.62 | 74.97 | 75.86 | 75.37 | 74.12 | 74.46 | 75.65 | 77.04 | 76.85 | 75.77 | 77.27 | 77.07
9/22/2010 | ######## | 75.89 | 76.83 | 77.04 | 70.71 | 76.55 | 74.61 | 72.84 | 75.67 | 74.92 | 74.12 | 77.07 | 77.86 | 77.47 | 76.53 | 76.39 | 76.1 | 76.06 | 76.74 | 76.29 | 74.49 | 75.88 | 77.49 | 79.16 | 78.46 | 77.49 | 78.25 | 79.2
9/22/2010 | ######## | 76.94 | 77.91 | 77.45 | 71.45 | 76.79 | 75.46 | 73.07 | 76.79 | 75.25 | 74.66 | 78.08 | 78.3 | 79.27 | 77.29 | 76.78 | 76.75 | 77.26 | 77.27 | 76.57 | 76.21 | 77.05 | 78.18 | 80.2 | 79.51 | 79.34 | 79.38 | 80.74
9/22/2010 | ######## | 77.79 | 77.91 | 78.15 | 70.89 | 76.79 | 76.64 | 73.83 | 76.83 | 75.97 | 74.26 | 79.34 | 79.45 | 80.85 | 78.22 | 78.55 | 79.05 | 78.94 | 78.32 | 76.84 | 77.92 | 78.35 | 78.61 | 81.41 | 80.02 | 80.15 | 80.43 | 80.99
9/22/2010 | ######## | 78.56 | 77.91 | 78.15 | 70.73 | 76.85 | 78.12 | 74.42 | 77.53 | 76.32 | 73.83 | 80.1 | 80.49 | 82.36 | 79.45 | 81.1 | 80.89 | 81.19 | 81.05 | 78.45 | 79.04 | 79.3 | 79.41 | 82.67 | 81.03 | 81.66 | 81.3 | 81.35
9/22/2010 | ######## | 78.56 | 77.91 | 78.94 | 70.73 | 77.58 | 79.91 | 74.89 | 77.61 | 76.83 | 74.19 | 79.92 | 80.78 | 82.83 | 80.46 | 82.54 | 82.36 | 83.65 | 83.13 | 79.77 | 80.63 | 79.43 | 79.79 | 82.98 | 81.14 | 82.05 | 81.97 | 81.83
9/22/2010 | ######## | 78.56 | 77.91 | 78.7 | 70.48 | 76.97 | 80.13 | 75.71 | 77.23 | 76.28 | 76.91 | 79.66 | 80.78 | 83.59 | 81.39 | 83.37 | 83.37 | 86.14 | 85.1 | 79.78 | 81.36 | 79.43 | 79.79 | 82.29 | 81.14 | 82.05 | 81.97 | 81.83
9/22/2010 | ######## | 78.56 | 77.91 | 78.14 | 70.27 | 76.78 | 81.58 | 75.81 | 76.83 | 76.05 | 78.43 | 79.66 | 80.78 | 83.59 | 82.44 | 84.27 | 84.45 | 86.79 | 86.32 | 80.37 | 82.34 | 79.43 | 79.99 | 82.29 | 81.14 | 82.05 | 81.97 | 81.83
9/23/2010 | ######## | 77.05 | 75.94 | 76.26 | 70.58 | 76.78 | 77.58 | 73.37 | 73.37 | 74.64 | 73.8 | 77.68 | 76.71 | 77.94 | 78.3 | 79.66 | 80.2 | 78.54 | 78.59 | 79.1 | 77.48 | 75.08 | 76.71 | 78.89 | 77.44 | 77.74 | 77.82 | 78.9
9/23/2010 | ######## | 74.31 | 73.52 | 74.34 | 69.47 | 76.78 | 76.83 | 71.81 | 73.1 | 72.2 | 73.57 | 75.42 | 76.71 | 76.17 | 76.68 | 77.25 | 77.5 | 75.92 | 77.14 | 77.94 | 75.18 | 73.36 | 74.44 | 76.12 | 75.44 | 76 | 75.38 | 76.13
9/23/2010 | ######## | 74.81 | 74.36 | 74.86 | 68.58 | 77 | 76.61 | 71.55 | 74.43 | 73.3 | 74.03 | 76.89 | 77.43 | 76.46 | 77.04 | 78.26 | 78.73 | 76.46 | 78 | 78.16 | 75.37 | 75.13 | 75.53 | 77.1 | 76.51 | 76.9 | 77.47 | 76.8
9/23/2010 | ######## | 75.63 | 75.25 | 75.54 | 68.79 | 77.62 | 76.22 | 73.18 | 75.66 | 74.45 | 74.27 | 77.32 | 77.5 | 77.07 | 77.76 | 79.3 | 80.17 | 77.21 | 78.7 | 78.54 | 76.78 | 76.38 | 76.38 | 78.72 | 77.51 | 77.31 | 78 | 78.29
9/23/2010 | ######## | 77 | 77.14 | 77.51 | 70.04 | 77.08 | 74.44 | 73.28 | 76.74 | 76.2 | 74.11 | 77.14 | 78.04 | 78.55 | 77.83 | 79.81 | 80.64 | 78.54 | 79.14 | 79.17 | 77.47 | 76.18 | 77.8 | 80.86 | 79.71 | 78.57 | 78.35 | 80.44
9/23/2010 | ######## | 78.15 | 78.63 | 78.84 | 71.18 | 76.79 | 74.78 | 73.75 | 76.83 | 76.53 | 74.36 | 78.19 | 78.69 | 80.56 | 78.66 | 79.05 | 79.84 | 79.67 | 79.51 | 79.77 | 78.72 | 77.29 | 78.84 | 81.29 | 80.14 | 80.98 | 80.38 | 81.68
9/23/2010 | ######## | 78.36 | 78.63 | 78.89 | 70.79 | 76.79 | 75.39 | 74.29 | 76.83 | 77.18 | 74.36 | 78.76 | 78.87 | 82.08 | 78.94 | 79.7 | 80.71 | 80.87 | 80.74 | 79.77 | 80.16 | 78.14 | 78.84 | 81.29 | 80.25 | 81.28 | 80.88 | 81.78
9/23/2010 | ######## | 78.36 | 79.2 | 79.59 | 70.92 | 76.93 | 76.63 | 74.9 | 77.51 | 77.31 | 74.36 | 79.56 | 79.77 | 83.19 | 79.77 | 81.1 | 81.93 | 82.31 | 81.57 | 80.31 | 80.8 | 78.96 | 79.28 | 81.75 | 81.12 | 81.84 | 80.86 | 81.78
9/23/2010 | ######## | 79.04 | 79.44 | 79.59 | 71.25 | 76.94 | 76.82 | 75.05 | 76.95 | 77.31 | 74.63 | 79.56 | 79.88 | 83.41 | 81.03 | 82.04 | 82.72 | 84.54 | 83.21 | 80.58 | 82.2 | 79.32 | 79.68 | 82.15 | 81.78 | 82.49 | 80.9 | 81.78
9/23/2010 | ######## | 79.16 | 79.44 | 78.86 | 70.83 | 76.81 | 76.58 | 75.05 | 76.83 | 77.31 | 77.23 | 80.31 | 79.88 | 83.41 | 81.21 | 82.33 | 83.3 | 83.88 | 83.03 | 80.58 | 82.47 | 78.59 | 79.68 | 82.15 | 81.75 | 81.49 | 80.56 | 81.44
9/24/2010 | ######## | 74.25 | 73.74 | 73.91 | 69.75 | 76.19 | 76.56 | 72 | 73 | 71.92 | 73.67 | 74.73 | 75.88 | 74.62 | 75.52 | 76.86 | 77.18 | 75.56 | 76.43 | 78.28 | 73.71 | 71.58 | 73 | 75.46 | 74.33 | 75.11 | 73.61 | 75.27
9/24/2010 | ######## | 74.31 | 73.85 | 73.95 | 69.75 | 76.19 | 76.41 | 72 | 73.1 | 72.21 | 73.93 | 74.37 | 76.21 | 74.52 | 75.49 | 76.14 | 76.75 | 74.89 | 76.1 | 77.63 | 73.61 | 71.64 | 73.29 | 75.29 | 74.26 | 74.97 | 74.14 | 75.18
9/24/2010 | ######## | 75.39 | 75.42 | 75.39 | 69.75 | 76.38 | 76.41 | 72 | 74.66 | 73.83 | 73.93 | 75.85 | 78.08 | 75.56 | 76.5 | 76.75 | 78.01 | 74.89 | 77.18 | 77.7 | 74.63 | 73.19 | 75.28 | 76.72 | 76.24 | 75.9 | 76.87 | 76.53
9/24/2010 | ######## | 76.1 | 76.31 | 76.61 | 70.02 | 77.4 | 76.83 | 72.35 | 75.99 | 74.74 | 73.93 | 77.4 | 78.58 | 76.21 | 77.4 | 77.11 | 78.44 | 76.55 | 77.3 | 78.51 | 75.36 | 74.64 | 76.21 | 77.46 | 77.35 | 76.97 | 78.03 | 77.85
9/24/2010 | ######## | 77.06 | 77.15 | 77.39 | 70.33 | 77 | 76.67 | 74.01 | 77.09 | 75.59 | 74.07 | 78.73 | 79.63 | 77.14 | 78.44 | 77.54 | 79.66 | 78.17 | 77.98 | 78.9 | 77.17 | 76.64 | 77.4 | 79.16 | 78.14 | 77.75 | 78.68 | 78.86
9/24/2010 | ######## | 78.06 | 78.17 | 78.65 | 71.13 | 76.92 | 77.54 | 74.52 | 78.16 | 76.73 | 74.72 | 78.87 | 80.71 | 78.84 | 79.56 | 79.23 | 80.1 | 78.86 | 78.97 | 79.52 | 77.96 | 77.78 | 78.85 | 80.53 | 79.55 | 79.09 | 79.33 | 80.21
9/24/2010 | ######## | 78.29 | 78.57 | 79.39 | 71.13 | 77.04 | 77.88 | 75.38 | 78.36 | 78.29 | 74.72 | 80.92 | 81.21 | 80.78 | 80.92 | 80.49 | 80.92 | 80.45 | 80.77 | 80.36 | 79.92 | 79.21 | 80.38 | 82.45 | 80.75 | 81.24 | 80.85 | 82.05
9/24/2010 | ######## | 78.95 | 79.49 | 79.86 | 71.13 | 77.72 | 78.65 | 76.19 | 78.94 | 78.82 | 74.05 | 82.58 | 82.18 | 81.86 | 81.43 | 82.22 | 82.83 | 82.33 | 81.7 | 80.84 | 81.81 | 80.7 | 81.33 | 83.44 | 81.82 | 82.7 | 82.17 | 83.12
9/24/2010 | ######## | 79.54 | 80.67 | 80.58 | 71.13 | 77.07 | 80.49 | 76.64 | 79.04 | 79.31 | 74.4 | 82.4 | 82.47 | 82.8 | 82.58 | 83.7 | 83.77 | 84.05 | 83.3 | 82.12 | 83.28 | 81 | 81.58 | 83.93 | 81.86 | 83.64 | 83.01 | 84.07
9/24/2010 | ######## | 79.79 | 80.88 | 80.2 | 70.62 | 76.88 | 81.52 | 76.64 | 78.35 | 78.9 | 77.64 | 82.08 | 82.47 | 83.19 | 83.44 | 84.27 | 85.39 | 85.34 | 84.74 | 82.19 | 84.03 | 81 | 81.58 | 83.93 | 81.86 | 83.64 | 83.01 | 84.1

## Slide 17: 2010: 9/27-9/30
9/27/2010 | 7:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 8:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 9:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 10:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 11:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 12:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 1:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 2:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 3:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/27/2010 | 4:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 7:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 8:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 9:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 10:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 11:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 12:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 1:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 2:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 3:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/28/2010 | 4:00:00 PM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/29/2010 | 7:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/29/2010 | 8:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/29/2010 | 9:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/29/2010 | 10:00:00 AM | 78.99 | 77.76 | 80.19 | 70.95 | 77.45 | 80.67 | 76.64 | 77.55 | 77.32 | 80.43 | 82 | 82.44 | 83.16 | 82.9 | 85.1 | 86.5 | 84.46 | 83.86 | 81.36 | 82.33 | 80.78 | 82.35 | 83.03 | 83.53 | 82.7 | 82.88 | 83.23
9/29/2010 | 11:00:00 AM | 79.93 | 80.01 | 80.48 | 70.86 | 76.41 | 77.33 | 76.22 | 78.57 | 78.61 | 73.8 | 81.32 | 80.06 | 79.16 | 77.36 | 78.51 | 78.37 | 78.11 | 78.13 | 79.22 | 77.76 | 78.54 | 71.26 | 79.85 | 81.1 | 81.32 | 81.54 | 81.87
9/29/2010 | 12:00:00 PM | 80.72 | 80.78 | 80.85 | 70.86 | 77.09 | 78.08 | 76.22 | 78.58 | 78.61 | 73.79 | 81.54 | 80.89 | 80.38 | 78.44 | 78.51 | 78.51 | 78.69 | 78.41 | 79.23 | 78.3 | 78.83 | 79.75 | 82.62 | 81.85 | 82.14 | 82.47 | 81.88
9/29/2010 | 1:00:00 PM | 80.72 | 80.78 | 80.85 | 70.86 | 77.09 | 78.13 | 76.22 | 78.58 | 79.09 | 73.79 | 82.51 | 80.89 | 81.54 | 79.16 | 79.88 | 80.38 | 79.48 | 79.24 | 79.23 | 79.84 | 79.88 | 80.01 | 82.88 | 82.64 | 82.84 | 82.48 | 81.88
9/29/2010 | 2:00:00 PM | 80.72 | 80.78 | 80.85 | 70.86 | 77.09 | 78.49 | 76.22 | 79.15 | 79.4 | 73.79 | 83.08 | 81.75 | 82.54 | 79.99 | 81.21 | 82.11 | 81.3 | 80.88 | 80.03 | 80.69 | 80.32 | 80.19 | 83.12 | 83.19 | 83.01 | 82.48 | 81.88
9/29/2010 | 3:00:00 PM | 80.72 | 80.78 | 80.85 | 70.86 | 77.09 | 79.19 | 76.22 | 78.98 | 79.4 | 74.58 | 83.7 | 81.75 | 83.12 | 80.92 | 82.36 | 82.62 | 82.96 | 83.16 | 80.79 | 81.61 | 80.95 | 80.82 | 83.72 | 83.6 | 83.82 | 82.48 | 81.88
9/29/2010 | 4:00:00 PM | 80.72 | 80.78 | 80.85 | 70.53 | 77.09 | 79.75 | 76.22 | 78.39 | 78.7 | 77.45 | 83.19 | 81.75 | 83.12 | 81.32 | 82.62 | 83.37 | 83.9 | 83.47 | 80.83 | 81.97 | 80.95 | 80.82 | 83.72 | 83.6 | 83.82 | 82.48 | 81.88
9/30/2010 | 7:00:00 AM | 79.74 | 79.17 | 79.23 | 70.3 | 77.09 | 78.79 | 75.46 | 76.35 | 77.25 | 74.03 | 80.67 | 79.3 | 78.51 | 78.87 | 81.79 | 81.79 | 79.02 | 78.58 | 80.11 | 78.71 | 76.89 | 79.22 | 81.16 | 80.29 | 80.46 | 79.95 | 80.26
9/30/2010 | 8:00:00 AM | 79.22 | 79.17 | 79.23 | 70.35 | 77.09 | 78.79 | 75.46 | 76.35 | 75.55 | 73.9 | 80.02 | 79.3 | 78.15 | 78.55 | 81.79 | 81.79 | 79.02 | 78.84 | 80.11 | 78.71 | 76.5 | 78.16 | 81.16 | 80.29 | 80.46 | 79.95 | 80.26
9/30/2010 | 9:00:00 AM | 79.22 | 79.91 | 79.23 | 70.75 | 77.1 | 79.68 | 75.46 | 76.86 | 76.42 | 74.43 | 79.12 | 79.34 | 78.48 | 78.91 | 81.79 | 81.79 | 79.09 | 79.41 | 80.21 | 79.58 | 77.86 | 79.5 | 81.64 | 80.72 | 80.92 | 80.45 | 80.68
9/30/2010 | 10:00:00 AM | 79.7 | 80.73 | 80.01 | 71.07 | 77.75 | 79.69 | 75.66 | 78.24 | 77.33 | 74.43 | 80.49 | 80.46 | 79.52 | 79.77 | 82.44 | 82.47 | 80.26 | 79.41 | 80.92 | 80.31 | 78.76 | 80.04 | 82.51 | 81.53 | 82.02 | 80.76 | 81.82
9/30/2010 | 11:00:00 AM | 80.02 | 80.9 | 80.55 | 71.07 | 77.02 | 79.69 | 76.23 | 79.2 | 78.25 | 74.43 | 80.6 | 81.39 | 80.06 | 80.53 | 82.87 | 82.62 | 80.65 | 79.41 | 81.58 | 80.31 | 79.24 | 80.67 | 83.52 | 82.33 | 82.14 | 80.97 | 82.74
9/30/2010 | 12:00:00 PM | 80.02 | 80.9 | 80.84 | 71.07 | 77.02 | 79.69 | 76.63 | 79.59 | 78.88 | 74.43 | 81.9 | 81.75 | 80.64 | 80.53 | 82.62 | 82.62 | 80.65 | 79.9 | 81.74 | 80.94 | 79.69 | 80.86 | 84.48 | 82.74 | 82.93 | 81.59 | 82.76
9/30/2010 | 1:00:00 PM | 80.02 | 81.74 | 80.84 | 71.07 | 77.02 | 79.69 | 77 | 79.59 | 79.46 | 74.43 | 83.01 | 81.75 | 80.74 | 80.53 | 82.62 | 83.01 | 81.47 | 80.23 | 81.74 | 82.53 | 80.93 | 81.12 | 84.55 | 83.07 | 83.02 | 82.37 | 83.05
9/30/2010 | 2:00:00 PM | 80.34 | 81.75 | 81.38 | 71.07 | 77.02 | 80.48 | 77 | 80.01 | 79.03 | 74.43 | 83.12 | 82.36 | 81.46 | 80.53 | 83.7 | 83.84 | 81.47 | 80.23 | 82.32 | 81.49 | 80.93 | 81.68 | 84.55 | 83.61 | 83.85 | 82.45 | 83.59
9/30/2010 | 3:00:00 PM | 80.82 | 81.75 | 81.65 | 71.07 | 77.02 | 80.68 | 77 | 80.4 | 79.44 | 74.43 | 83.12 | 82.58 | 81.46 | 80.92 | 84.34 | 84.56 | 81.47 | 80.23 | 82.57 | 81.1 | 80.93 | 81.68 | 84.55 | 83.61 | 83.85 | 83.22 | 83.59
9/30/2010 | 4:00:00 PM | 81.15 | 81.75 | 81.65 | 70.64 | 76.56 | 81.57 | 77 | 80.24 | 79.45 | 74.31 | 83.12 | 82.58 | 81.46 | 81.36 | 83.52 | 83.41 | 81.47 | 80.23 | 82.57 | 81.1 | 80.93 | 81.68 | 84.55 | 83.61 | 83.42 | 82.39 | 83.59

## Slide 18: Days ≥ 780 F in 2010* 10 2nd floor classrooms with the most complete (not the worst) data
*Probably higher for many rooms when entire year is included
Room | 227 | 228 | 229 | 230 | 232 | 234 | 235 | 236 | 237 | 238 |  | 
Days ≥ 78 F | 35 | 35 | 31 | 27 | 27 | 37 | 34 | 35 | 32 | 33 |  | 
% school year | 19.4 | 19.4 | 17.2 | 15.0 | 15.0 | 20.6 | 18.9 | 19.4 | 17.8 | 18.3 |  | 
Average for these classrooms:
18% of the school year ≥ 780 F

## Slide 19: Was 2010 a Fluke? 2011: 5/16-6/23

## Slide 20: MS Teacher survey: “What symptoms have you experienced on high heat days?”
“There were days where I seriously thought I might pass out. I'm a young, healthy, fit guy.”
Symptom | % Response
Inability to concentrate or sluggishness | 86%
Excessive sweating | 78%
Excessive thirst | 69%
Headache | 62%
Dizziness/ light-headedness | 62%
Nausea | 38%

## Slide 21: Summary
Excessive classroom temperatures are frequent, persistent, and widespread
Work environment is unhealthy
Impact on learning is likely to be significant

## Slide 22: RSC work to date
2009-2011: Subcommittee looked at non-AC options
  What didn’t work: ceiling fans, holding classes elsewhere
  What won’t work: tinted windows, white roof, atrium cooling, window AC units, portable room AC units
2011: Air conditioning study
  Review by subcommittee, including town and citizen representatives
2012-13: Bid documents, RFP, award contract subject to funding

## Slide 23: The Plan
Roof-top AC units, with coolant delivered to existing classroom heater/air-exchange units
  Best combination of cost, efficiency, and construction and operational flexibility
  No new ductwork required
  All interior work can be completed over the summer
  Centralized control, classroom adjustment within set parameters

## Slide 24: Costs
Total cost: $852, 395
  Bonded over 5 years
  Each town’s yearly share dependent on enrollments
  Estimated annual operational cost ~$11,000 (May, June, September)
 | Principal | Interest | Total
Dover | $467,273 | $17,960 | $485,222
Sherborn | $385,727 | $14,620 | $400,347

## Slide 25: Next Steps
5/4: Sherborn TM
5/6: Dover TM
5/14: Sherborn ballot (debt exclusion)
Construction begins 6/13
Completed w/o disruption to school start
Thank you!